	PSGSG 13-14 / 030
	Product Specifications

For

SWITCHING CONTACTS
	Drg. No.
	RD DG 4 35 0617 0511,RD DG 4 35 0617 0312

	
	
	Date
	14.11.2014

	
	
	Product
	GSM 400

	  1.0

2.0

3.0

4.0


	 Application                                             :  Switching Contacts  for Gas Insulated  
                                                                     Switchgear Equipment 

 Configuration                                        : 1.  Sintered W-Cu (70-30 %), welded (by   

                                                                     electron Beam welding process) to the  

                                                                     high conductivity copper–Cr alloy. 
2. Sintered W-Cu (80-20 %)                 

                                                                3.  Machined to drawing dimensions.

 Quantity                                                : 1) Switching contacts-I as per
                                                                 drawing RD DG 4 35 0617 0511:10 No.s

                                                                 2)Switching contacts-II as per

                                                                 drawing RD DG 4 35 0617 0312:10No.s
Specifications:
1. Dimension Drawings          :  Refer Drg No.  RD DG 435 0617 0511,RD DG 435 0617

                                             0312 
2. Material:                          :  Tungsten-Copper, Cu-Cr alloy
(a). W-Cu
A sintered matrix of W-Cu (70-30 %) shall be produced by PM technique. The sintering shall be carried out in neutral or reducing atmosphere. The ingredient (powders) shall have high purity. 

(b). Cu-Cr Alloy

Copper :  99 %,  Chromium  : 1 %.

This alloy shall be made using fine alloying practices so as to minimise occlusion of gases. The oxygen content shall not exceed 100 ppm. Vacuum metallurgy for alloying is preferred. The copper used for alloying shall be 99.97 % pure. Electrolytic grade is preferred. Electrical conductivity of Cu-Cr Stem shall be greater than 82 %. (IACS)


	1/2
	PSGSG 13-14 / 030
	
	Signature



	PSGSG 13-14 / 030
	Product Specifications

For

SWITCHING CONTACTS
	Drg. No.
	RD DG 4 35 0617 0511,RD DG 4 35 0617 0312

	
	
	Date
	14.11.2014

	
	
	Product
	GSM 400

	5.0

6.0

7.0

8.0

9.0

  
	Electron Beam Welding (EBW): 

The component shall be finished to size before electron beam welding at the interface. The interface will be between High conductivity copper- Cr alloy and W-Cu Tip. The interface shall be welded to full depth. The welding joint between Cu-Cr alloy and W-Cu tip shall exhibit minimum contact resistance. The Component shall be free from dirt, grease and loose particles. 

Qualifying Requirements:
The supplier shall be of national / International repute with proven record and should have supplied arcing contacts for switch gear applications. The supplier must submit along with the quotation a few references to whom the supplier has supplied a similar material. 
Tests:

(a). Dimensional : All dimensions shall comply to drawing measures.

(b). The component shall be subjected to micro-ohm measurement test, using 100 A DC  

      source and shall measure less than one micro-ohm at the welding interface.
Packing : 

The contacts shall be packed in high density cardboard boxes, with a primary wrapped in polyethylene and packed individually in dust free boxes after degreasing. The component shall be guaranteed against all manufacturing defects.

General :

1. Surface finish of the components shall be at least RA 1.6.

2. The component shall be free from dirt, grease and loose particles.
In case of doubts in drawings or specifications the supplier shall contact BHEL for clarifications.

	2/2
	PSGSG 13-14 / 030
	
	Signature




