Page 4 of 5/spec no-7182


BHARAT  HEAVY ELECTRICAL LIMITED

(Work Engineering & Services)

Unit : JHANSI

EQUIPMENT



 :  Transformer oil Filtration Plant (3 KL)
SPECIFICATION


 :  7182
ITEM NO.



 :   ME-1/5/2639
LOCATION



 :  Traction Transformer Shop(Bay-6)

QUANTITY 



:    One No.

                    This plant is to be suitable for processing / conditioning of Shell Diala  transformer insulating oil having specifications as per IEC 296( Class- II A )& VDE 0370(Class A ) for 3 phase ACEMU (Freight Loco) transformers. The properties of shell diala oil will be as given below.

1.
Appearance 


-
Not cloudy , free of solid and water

2.
Density (@15 °C).

-
0.877 Kg / L

3.
Kinematic Viscosity

-
800 mm ²/S (- 15 °C.), 

-
25 mm ²/S   (20°C),

-
11 mm ²/S    (40°C)

4.
Flash point (PMCC)

-
136°C.

5.
Pour point


-
Less than    (- 60°C)
6.
Dielectric strength (BDV)
-
More than 60 Kv

7.
Dielectric dissipation factor
-
0.001 (At 90°C).

This unit is to be of package type mounted on the common frame with necessary lifting lugs for easy portability. This plant is to be capable of processing the transformer oil at 3000 liters per hour. The control range of in flow / outflow should be variable from 1500 liters per hour to 3000 liters per hour. The plant shall be robust in design &suitable for continuous operation in an ambient temperature of 48°C.

             The equipment is to be guaranteed for the following condition of oil after treatment:

(A)
Moisture removal      




:               

Maximum initial moisture content


:    100 ppm

Moisture content after one pass


:    Less than 5ppm
(B)
Gas content

Initial gas content before filtration


:    10% by volume


Initial gas content after one pass of filtration
:    0.1% by vol.

(C)
Filtration fineness




:    0. 5Micron after   

                                                                                                      Filtration
(D)
Processing temperature



:    40 to 70 degree Celsius
(E)
Improvement of dielectric strength (BDV)

:    More then 70 Kv in one  

                                                                                                     pass

The oil filtration plant shall be designed for high vacuum & low temp. of oil for achieving required results as mentioned above.

Configuration of the plant :-
The plant will consist of the following major components

1.
A pre filter- for protection of gear pump, having system of easily replaceable filter element.

2.
An oil inlet gear pump - highly reputed make like M/s Maag with flow control valve & pressure safety valve.

3.
The steam heating system -  the heater to be steam heated type suitable for operation at low pressure of 3.5 kg/ cm² & capable of raising temp. up to 90°C in single pass. The heater & steam & condensate line to be suitably lagged as to maintain the surface temperature with in 05°C above ambient temp. The steam heating system along with pressure reduction station from 10 kg /cm². to less than 3.5 kg /cm². is to be provided and connected to our existing steam line. The pressure reduction station shall be complete with steam separator, strainer, bypass arrangement, safety valve, in let & outlet pressure gauges. Suitable arrangement to regulate & maintain the outlet temperature shall be provided.

4.
Filtration system-   A cartridge type filter is to be provided to filter 3000 L.P.H. of oil to 0. 5 micron filter fineness. The filter is to be suitably designed for easy replacement of cartridges.

5.
Degassing column-The degassing chamber shall be two stage type of adequate      capacity for dehydration / deaeration of the transformer oil at specified rate. It shall be of totally welded construction in two halves and to be provided with, illuminating lamp, sight glass along with low level and high level switches for controlling the flow of oil. The low level switch will be connected to make off centrifugal pump & high level to make off inlet gear pump.

6.
Vacuum system (degassing)-A suitable Roots-Rotary Vacuum Pump combination system is to be provided to obtain vacuum level of less than 0.15 mbar in the second stage of degasser. The vacuum pumps should be of reputed make like PFEIFFER/ LEYBOLD Germany / SHINCO SEIKI / TOSHO Japan. The capacity of pump is to be mentioned in the offer. Calculations in support of justification vacuum pumps capacity combination 

7.
Discharge pump-Centrifugal mono block ( Glandless type ) Pump of reputed make for sucking oil under vacuum in the degasser of capacity 3000 L.P.H. and 10 meter head discharge.

8.
Electrical control panel-Base mounted comprising of all necessary switches, lamps, contactors overload protection for motors and HRC fuses and relays etc. and all necessary instrumentation to be installed. A mimic diagram is to be provided. The system must be complete with all inter locking devices to guarantee the operation in right sequence and automatically stopping where there is a trouble during the operation for safety of the plant The switch panel to be mounted on the plant .

The system is also to be fitted with the following:

(a)
A magnetic filter before outlet point.

(b)
All necessary devices such as manometer at inlet, manometer to measure oil pressure before and after cartridge filter.

(c)
The vacuum gauge on degassing column.

(d)
Vacuum Gauge (Mcleod type) range 10 torr to 0.01 torr.

(e)
A pirani vacuum gauge on control panel.

(f)
Thermostat to switch off vacuum pump incase of cooling water failure.

(i)
A sucbac valve on Vacuum pump.

(j)
Airing Valve 

(K)
Automatic bypass valve for root pump.

(l)
A flow meter with totalizer.

(m)
Dial thermometer, one at heater inlet and one at heater outlet.

(n)
Necessary oil and vacuum valve will be Ball type only.

(o)
Oil sampling valve at plant inlet and outlet to be provided.

(p)
Isolation valve at plant inlet and outlet.

(q) A temperature and vacuum recorder to be provided.

(r) Fool proof temperature controlling system for oil to be provided in the circuit so that oil temperature should not increase more than 70°C. 

GENERAL CONDITIONS:
1.
Hydraulic, pneumatic and oil piping should be preferably metallic except places where flexible piping are essential. All the pipes required for the same shall be included in the standard scope of the machine.

2.
Detailed catalogues, sketch/ photograph of the machine and accessories/ attachments should be submitted with the offer.

3.
Vender to submit along with their offer:

-
Total weight of the equipment.
-
Quantity of chilled water & normal temperature water required for cooling of condensers and vacuum system.

-
Floor area required (Length, Width, Height ) for complete machine & accessories shall be mentioned.

4.
 The plant will be inspected at supplier's work and performance as per parameter shall be checked. Training for operation shall be given by supplier’s at BHEL works. 

5.
The supplier shall commission the plant at BHEL Jhansi. Erection and commissioning charges to be quoted separately in price bid. Necessary civil work shall be done by BHEL based on supplier’s drawings. All tools/ tackles for erection and commissioning shall be brought by supplier’s   

6.
The plant shall be guaranteed for trouble free performance for a period of 24 month from data of commissioning.

7. 
Details of all bought out items along with their specifications, technical literature,/leaflet in original along with complete address of supply source shall be submitted.

8.
A detailed manual containing all technical details circuit diagram operation and maintenance procedure and spare part list shall be given properly printed on a computerized format and neatly binded shall be provided by supplier in three copies. Tool kit shall be provided by supplier.
9. Painting of machine / Electrical panels: RAL 6011 Apple green (Polyurethane paint)
 10.
Test to be carried out at BHEL works while commissioning the equipment:

Oil conditions shall be obtained as mentioned in our specification 

QUALIFYING CONDITIONS

Only those vender, who have supplied and commissioned at least 10 numbers Oil filtration and degassing plant of mentioned specifications or higher Capacity  for similar application in the past ten years and such machine is presently working satisfactorily for more than one year (more than six month if supplied to BHEL).after commissioning should quote. 
The following information is to be submitted by the vender about the companies to whom similar machines have been supplied. This is required from all the venders for qualifications of their offers.

1. Name of the customer/ company where similar machine is installed

2. Complete postal address of the customer

3. Year of commissioning

5. Name and designation of the contact person of the customer

6. Phone, Fax No. and E-mail address of the contact person of the customer

7. Performance certificate from the customer regarding satisfactory performance of the  machine supplied to them.
	Prepared By
	Approved By

	V.Kevre

Dy.Mgr(WEX)
	S.J.C.

DGM(WEX)
	A.K.S.

AGM(WEX/FBM)
	        V.K.A.

AGM(TRM/TRP)
	       A.K.

AGM(ENGG.)


