[image: image5.png]EELA

nﬂn




BHARAT HEAVY ELECTRICALS LIMITED

HYDERABAD

TECHNICAL SPECIFICATIONS 
PART B

	PART-B1
	FINAL EFFLUENT TREATMENT PLANT

	PART-B2
	EFFLUENT TREATMENT PLANT BLOCK08

	PART-B3
	EFFLUENT TREATMENT PLANT BLOCK03

	PART-B4
	EFFLEUNT TREATMENT PLANT – MOTOR TRANSPORT



~

BHARAT HEAVY ELECTRICALS LIMITED

HYDERABAD

TECHNICAL SPECIFICATIONS OF

 FACTORY FINAL EFFLUENT TREATMENT PLANT
	SL.NO
	DESCRIPTION
	
	PAGE NO.

	1
	INTRODUCTION
	2

	2
	PRESENT STATUS
	3

	3
	BASIC DATA
	4

	4
	SCOPE OF WORK 
	5

	5
	PROPOSED SCHEME OF CONTRACT
	7

	6
	SIZES AND SPECIFICATIONS OF VARIOUS UNITS (CIVIL, ELECTRICAL &MECHANICAL WORKS)
	8

	7
	SPECIFICATION OF ELECTRICAL WORKS
	17

	8
	DOCUMENTATION
	
	21

	ANNEXURE
	
	
	

	1
	 ETP SCHEMATIC LAYOUT (FIGURE-1)
	23

	2
	TOLERANCE LIMITS FOR DISCHARGE FROM ETP (ANNEXURE-1)
	24

	3
	 LIST OF RELEVANT CODES & STANDARDS (ANNEXURE-2)
	25


INDEX

Deviations from the specifications if any, shall be clearly brought out by the bidder with sufficient explanation separately at the end, giving reference to the clause number in the specification. Otherwise it will be presumed that the tender in total conformity is accepted by the bidder.

FINAL FACTORY EFFLUENT TREATMENT PLANT
1. 
INTRODUCTION.

The BHEL Hyderabad unit was set up in 1963 and started its operations with manufacture of Turbo-generator sets and auxiliaries for 60 and 110 MW thermal utility sets. Over the years it has increased its capacity range and diversified its operations to many other areas. 

The factory is situated at Ramchandrapuram, approximately 23Km.  from Secundrabad Railway Station. At present there are about 6000 employees working in the plant. The township is situated adjacent to the factory having population of approximately 30000 with about 4600 staff quarters. 

The manufacturing facilities at BHEL, Hyderabad include:

i. TC&GT  -Block-01

ii. Turbo Generator & Boiler feed pumps- Block-02

iii. Switch Gear and Breaker  Block-03

iv. Foundry & Pattern making shop – Block-04, 05 & 09

v. Heat Exchanger/Fabrication-Block-06

vi. Tool Room Block-07

vii. Heat Treatment and common work shop –Block-08

viii. Pump manufacturing block –70

ix. Ball Mill & Oil field Equipment – Building –51

x. Services Department

· Motor Transport

· Acetylene Plant

· Producer Gas Plant

· Boiler House

· Power Generation (DG Sets)

· Canteens

While manufacturing the above products, around 600 KL of Industrial Effluent is being generated per day and is being sent for treatment at Sewage Treatment and Disposal Plant (STDP) along with domestic effluent having an inbuilt capacity of 2 MGD. This treatment plant is situated 5 Km away from BHEL Township. This plant also treats the sewage coming from BHEL township and adjoining colonies.

Being an Engineering industry, pollution may be due to oil spillage and solid waste generated. Certain blocks like 08 block and 03 block where metal coating and surface cleaning operation take place, effluent containing metals, cyanide etc. are generated. Besides service areas like Producer gas plant, Acetylene gas plant, Boiler house etc., generate process specific waste.

The water requirement for the plant and township is met from the Manjira river. The raw water is generally low in turbidity. The average water requirement for entire BHEL complex is 8200 m3/day. Out of this, 1031 m3/day of water is required for plant operations, while 7200 m3/day of water is used in the BHEL residential colony. Approximately 600 KL/day effluent is generated from the plant of which 480 KL/day is from sewage along with canteen waste. The rest arises from the various processes.

Due to the shortage of water, the availability of water has been restricted. It was observed that maximum effluent was generated during the shift changes. The effluent arising from various bays are diverted to the factory sewage line and the combined effluent is then taken to the Sewage treatment plant. 

2. PRESENT STATUS

While manufacturing  various  products in  BHEL, R C Puram,   Hyderabad Plant, 600 KL of  effluent is being generated from various sources.  Sewage and canteen washing contribute around  480 KL/day  the rest, from industrial processes like Pickling, Producer gas plant, Electroplating,  machining etc. The effluent consists of organic matter, heavy metals like chromium, Nickel, Iron, Cyanide and Phenols.

 The combined effluent from plant is mixed with the domestic sewage from the township and  is at present being treated at the existing Sewage Treatment and Disposal. This plant is at a distance of about  5 Km away. 

However, pollutants like heavy metals and cyanide cannot be effectively treated in the plant. Ingress of cyanide, heavy metals, phenols above prescribed standards results in stopping of  the  biological activity of the Sewage Treatment Plant. This results in higher BOD at the outlet of STDP. Chromium and Nickel concentrations may be towards higher side in the final discharge from the STP.

Hence the need was felt to have a separate Effluent treatment plant for treating the effluents from the factory. 

The Existing drain from the factory carrying the industrial effluent leaves the factory boundary near the J Gate. This drain can be intercepted and the effluent taken to the proposed Final Factory Effluent Treatment plant for treatment. This drain is located at approximately (-) 4.0m from ground level. However the agency has to inspect the site to ensure the invert level of the inlet pipe near the ETP site and also treated water receiving drain.
Sewage from plant (washings, canteen etc) after screening and Oil and Grease removal can be treated in the Sewage Treatment Plant to be designed and set up. This would have the following advantages:

a) As the specific pollutants would be treated at source, load on the STP would be less hence increasing the efficiency.

b) The volume of effluent to be treated will be low, hence small size plant would be  required saving in cost.

The proposed Final ETP would enable:

1.  To comply with the norms as stipulated by Pollution  Control Board.

2.  To make use of existing facilities/system to the extent possible.

3.  To have more cost effective system ensuring easy and economical maintenance.

4.  Shall be odour free operational as surrounding areas are residential.

5. Shall have at its outlet a sump with pumping arrangement (for later use of pumping back treated water into the factory for horticulture purposes.
3.0 BASIC DATA: 

The basic data considered for preparing schematics and sizing of unit operations of effluent treatment plant are given below:
a) Wastewater quantity: 600 m3 /day 

b) Characteristics of raw wastewater::

TABLE: CHARACTERISTICS OF RAW WASTEWATER

	S.N.
	Parameter
	Concentration*

	1
	pH
	6.5-7.5

	2
	Total Suspended Solids (TSS)
	250 

	3
	BOD (3 days at 27 0 C)
	                    100 - 200 (avg. 150 mg/l)

	4
	COD
	500-1000


*All parameters except pH expressed in mg/l

c) Characteristics of treated wastewater: The expected characteristics of the treated wastewater on adopting the scheme of treatment given under S.N. 5 are as given in table below:
TABLE: CHARACTERISTICS OF TREATED WASTEWATER 

	                                             Sr. No.
	Parameter
	Concentration*

        After TREATMENT

	1
	pH
	6.5 - 8.0

	2
	BOD (3 days at 27 0 C)
	< 30

	3
	TSS
	< 50

	4
	COD
	< 250


 *All parameters except pH expressed in mg/l

4. 
SCOPE OF CONTRACT
Scope of work shall broadly include design, construction, supply, erection and commissioning of Final Effluent treatment plant & operating the plant for a period of 2 years as per conceptual design and specifications. The tenderer should give the treated effluent quality confirming with the Andhra Pradesh State Pollution Board Standards (consent condition), as well as the parameters specified in Schedule VI of Environmental Protection rules 1986 (annexure-1) 
The following items are included within the scope of work :
a)  All the civil works and structural fabrication works of the treatment plant as per the detailed description of the civil works and generally as per the scheme provided. Detailed drawings with tentative levels of individual structure are also to be prepared. The contactor shall get the detailed civil and Engineering drawing approved by BHEL prior to initiation of civil work at site.  Proposed scheme of the Final ETP is enclosed in Figure- 1. The sizing and specifications given below are indicative only. The tenderer may cross check the sizing/broad specifications and modify, if required, to meet the quality of treated effluent. 
b)  Supply, erection and commissioning of all the equipment's required for the treatment plants as per the individual equipment's specifications and details given herewith.
c) The scope of work includes all necessary civil works, like construction MCC / Pump room, panel foundation, cable trenches cable supports, pipe supports, lighting of pump house etc. complete. The scope of work also includes in providing the puddle insert drawings as required for each unit operation of the Treatment Plant as per the envisaged scheme & layout plan.
d) The scope of work also includes de-linking the delivery of the existing Main drain near J-Gate, and connecting the drain to the proposed holding tank, this being the first level of the unit operation of the Final Effluent treatment plant and re-linking the final treated discharge line to the Main drain.
e) Obtaining all necessary statutory approvals from Andhra Pradesh State Pollution Control Board and other statutory bodies for construction and commissioning are included in the scope of work of contractor.
f)   The Horse Power (HP) of all the pumps, blower etc. shown are indicative. The actual HP shall be furnished by the contractor to meet the specified flow and head.
g)  Documentation shall be furnished as per clause 8.0. 
h)  All temporary sheds, offices, go downs etc., required for storage of materials and for contractors supervisory personnel at site is the scope of the bidder. The required equipments and materials are to received and stored by the bidder and to be issued as and when needed for installation.
i)  Other general terms and conditions as applicable for similar contracts for Civil, Mechanical and Electrical  work at BHEL, Hyderabad.

j)  All materials required for civil works & structural/fabrication works  (Cement, steel,  paints & structural steels etc.)  included in the vendors scope. However cement and steel will be issued by BHEL on cost recovery basis.
k)  BHEL will provide Electric power & Water at free of cost. The agency should make necessary arrangement for tapping from the approved source.
5.0. 
PROPOSED SCHEME OF TREATMENT:

The Final effluent from the plant is carried  through the industrial drain which exits the factory near the J Gate. The drain would be intercepted outside the J- Gate on the left side of the gate and diverted to the proposed Treatment Plant for treatment. The treated effluent which would meet the requirement of Schedule VI of Environment Protection rules would be discharged in to the drain .
The proposed scheme of Effluent Treatment Plant would consist of the following units and as indicated in Figure-1. Though not shown in the layout scheme, Plant bye pass shall be ensured in the event of maintenance. Sizing and specifications of unit operations given below are indicative only. The vendor may cross check and modify the size and rating, if required to meet the quality of treated  effluent.  
The Effluent Treatment Plant will consist of: 

1. Bar screen

2. Oil & Grease trap

3. Holding/Equalization Tank complete with aeration grid for mixing to avoid settling of solids
4. Primary clarifier

5. Aeration tank complete with aeration grid, diffuser and blower

6. Secondary clarifier

7. Sludge drying bed

8. Flow Measuring device
9. Sump for collection of treated water

6.0 SIZES AND SPECIFICATIONS OF VARIOUS UNITS (CIVIL, ELECTRICAL &            MECHANICAL WORKS) FOR THE PROPOSED PLANT.

6.1  Civil Works:

Specification Table  No. 6.1.1
	UNIT
	SCREEN CHAMBER I

	Duty
	For removal of coarse  floating matter

	No. of units
	One

	Size
	0.5 m x 0.8 m SWD and length of 5 m (inlet of pipe is at ( – ) 4.0 m)

	MOC
	RCC M-25


Specification Table  No. 6.1.2

	UNIT
	OIL & GREASE TRAP

	Duty
	To remove  oil and grease

	Number of Units
	One

	Size
	2.5 m X 2.5 m X 2 m SWD (invert level of drain is at (– )4.0 m)

	MOC
	RCC M-25

	Make
	KSB/ Kirloskar / Sulzar or equivalent


Specification Table  No. 6.1.3
	UNIT
	HOLDING/EQUALISATION TANK

	Duty
	To attenuate variations in flow and characteristics of wastewater.

	Number of Units
	One

	Size
	7.8 m X 7.8 m X 2.5 m SWD + 0.5 m FB

	MOC
	RCC M-25


Specification Table No.6.1.4

	UNIT
	PRIMARY SETTLING TANK

	Duty
	To enable solid liquid separation 

	No. of units
	One

	Size         
	6 m  internal dia X 2.5 SWD + 0.5 m FB sloping base towards the center with sludge wall as per requirement of the equipment supplied

	MOC
	RCC M-25


Specification Table No. 6.1.5

	UNIT
	AERATION TANK

	Duty
	To enable oxidation of the wastewater

	Number of Units
	One 

	Volume                    
	10.35 m X 10.35 m X 4.2 m SWD + 0.5 m FB

	MOC              
	RCC M-25


Specification Table No.6.1.6

	UNIT
	SECONDARY SETTLING TANK

	Duty
	To enable solid liquid separation 

	No. of units
	One

	Size         
	6 m  internal dia X 2.5 SWD + 0.5 m FB sloping base towards the center with sludge wall as per requirement of the equipment supplied

	MOC
	RCC M-25


Specification Table  No. 6.1.7
	UNIT
	SLUDGE DRYING BEDS

	Duty
	For dewatering and drying of sludge.

	Number of Units
	Two (to be used in a cyclic manner)

	Size
	3.0 m X 7 m X 0.8 m each +0.3 m FB

	MOC
	Base in PCC and walls in brick work.


Specification Table  No. 6.1.8

	UNIT
	SUMP

	Duty
	To collect treated effluent

	Number of Units
	One

	Size
	10.0 m X 10.0 m X 2.0 m SWD  + 0.5 m FB

	MOC
	RCC M-25


6.2 Mechanical works:

Specification Table No. : 6.2.1

	UNIT
	SCREENS

	Duty


	To retain coarse matter in wastewater  

	No. of units 

	Two ( coarse screen)

	Screen spacing
	10 mm center to center

	Size


	10 mm thick and 50 mm deep

	 MS Raking arm

	1 no. 2 m long

	MOC


	MSEP.


Specification Table No. : 6.2.2

	UNIT
	PUMPS

	Duty


	To pump wastewater from equalization tank to Primary clarifier

	No. of units 


	Two (1 W + 1 S at peak conditions)

	Capacity


	 25.0 cum/hr. 

	Head


	 12 m.

	Type


	Submersible pump 


MAKE  -   KSB / KIRLOSKAR / SULZAR  or  equivalent
Specification Table No. : 6.2.3

	UNIT
	API Type oil seperators

	Duty

	To enable skimming of oil floating on the surface of Oil & Grease tank                            

	No. of units 

	 One  

	Size                            
	Consisting of 80 mm dia MS pipes 2 nos. with perforations and tilting gear mechanism for skimming of oil.   

	MOC


	 Chevron type UV treated PVC


Specification Table No. : 6.2.4

	UNIT
	Clarifier Mechanism

	Duty

	To provide effective separation of organic floc from effluent.                            

	No. of units 

	 Two  

	Size                            
	Clarifier mechanism shall be suitable type for 6 m dia and 2.5 m SWD tank for fixed bridge, center drive mechanism with feed wall system.    

Scraper arm speed shall be 4 RPH.

The central shaft directly coupled through a reduction gear box of Radicon / Elecon /Shanthi  or equivalent make.

	Make

	 HDO/Voltas/INAVARA or Equivalent


Specification Table No. : 6.2.5

	                                UNIT
	AERATION GRID FOR HOLDING/EQUALISATION TANK

	Duty
	To bubble air for mixing and to avoid solids from settling

	No. of units
	One complete with piping network and suitable blower

	Size
	To suit size of equalization tank. 

	Type
	Piping network with header and laterals.

	MOC
	HDPE / PVC.


Specification Table No. : 6.2.6

	UNIT
	PUMPS

	Duty


	 To pump wastewater for onward treatment. 

	No. of units 


	 Two ( one as 100% stand-by )

	Capacity


	 25.0 cum/hr. 

	Head


	 8 m.

	Type


	 Non clog, self priming centrifugal pumps. 


Specification Table No. : 6.2.7

	UNIT
	BLOWERS

	Duty


	 To supplement air to the air grid.  

	No. of units 


	 Two ( one as 100% stand-by) 

	Rating


	 12.5 HP each; 200 – 250 m3/hr @ 0.5 kg/cm2 

	Type


	 Twin lobe rotary type.


Specification Table No. : 6.2.8

	UNIT
	AERATION GRID FOR AERATION TANKS 

	Duty
	To supply air from blower to diffusers.

	Number of Units
	One

	Size                     
	To suit size of aeration tank.

	MOC              
	PVC/HDPE 


Specification Table No. :6.2.9

	UNIT
	DIFFUSERS

	Duty
	To supplement air in aeration tank for bio-chemical oxidation.             

	No. of units
	40

	MOC
	EDPM rubber fine bubble diffusers.


Specification Table No. : 6.2.10

	UNIT
	SLUDGE RECIRCULATION PUMP

	Duty


	 To recycle sludge from settling tank to aeration tank. 

	No. of units 


	 Two ( one as 100% stand-by )

	Capacity


	 10.75 cum/hr. 

	Head


	 10 m.

	Type


	 Non clog, self priming centrifugal pumps. 


Specification Table No. : 6.2.11

	UNIT
	RATE OR FLOW METER

	Duty


	 To measure the rate of flow  

	No. of units 


	 One

	Type


	 Suitable flow meter (Electro Magnetic) to measure instantaneous and cumulative flow with digital display. (0-700 KLD). Make Forbes Marshall / Endress & Hauser. 


Specification Table No. : 6.2.12

	      Unit
	Control Unit

	Duty
	For operation and protection of all electrical starters.

	Incoming
	MCCB of adequate rating, ammeter, voltmeter, copper bus bar and phase indicating lamps.

	Out going
	Contactors of suitable rating of DOL type for motor rating up to 10 HP and Star-Delta type for motor ratings above 10 HP, thermal overload relay with built-in single phase presenter and HRC fuses for extra protection.

	Make
	All electrical items shall be of L&T, English Electric, GEC, Crompton, IMP, MECO or Siemens.

Separate panels shall be provided for each of the streams being fed to the RO

	Electrical cabling 


	All interconnecting cabling within ETP shall be in PVC insulated, armored /unarmored, aluminum conductor of standard make. Cabling, as far as practicable, shall be underground.


Specification Table No. : 6.2.13

	UNIT
	INTER-CONNECTING PIPING AND VALVES


	SI.

No.
	From
	To
	Size
	Material
	Valves

	
	
	
	mm
	
	

	1
	Bar Screen
	Oil & Grease Trap
	150 Dia
	CI insert- l no
	-

	2
	Oil & Grease Trap
	Holding /Equalisation Tank
	150 Dia
	CI insert- l no
	-

	3
	Holding /Equaliation Tank
	Primary Settling Tank
	150 Dia
	CI insert-l no
	-

	4
	Primary Settling Tank
	Aeration Tank
	150 Dia
	CI insert – 2 no HDPE
	1 no.125mm

sluice valve

	5
	Aeration tank
	Secondary Clarifier
	150 Dia
	CI insert- 2 no, HDPE
	1 no. 125 mm

sluice valve

	6
	Secondary Clarifier
	Flow measuring device
	-
	-
	-

	7
	Flow measuring device
	Sump
	-
	-
	-

	8
	Sump
	Final Main Drain
	500 x 800 SWD
	RCC M-25

Open Channel
	-

	9
	Clarifier sludge

well
	Suction of sludge

pump
	150 Dia
	HDPE
	2 nos. 125mm

sluice valve

	10
	Delivery of

sludge pump
	Sludge drying

beds/aeration tank
	150 Dia
	HDPE
	8 nos. 125mm

sluice valve

	11
	Sludge drying beds
Filtrate
	Holding/Equalisation   Tank
	100 Dia
	Stone Ware

Pipe
	


Specification Table No. 6.2.14

	UNIT
	ERECTION & COMMISSIONING

	Duty
	To erect the Final Effluent Treatment Plant (FETP). After erection of the FETP, the entire plant shall be commissioned to obtain the desired results. An operation and maintenance manual (3 copies) shall also be provided to the client. Necessary approval / clearance shall be obtained from the statutory authorities.


Specification Table No. 6.2.15

	UNIT
	Operation & Maintenance

	Duty
	The FETP has to be operated and maintained for a period of 24 months after obtaining the desired results / approval from the statutory authorities. All consumables, treatment chemicals, labour, repair and maintenance for regular running of the FETP shall have to be borne by the tenderer. Periodical monitoring of treated effluents from PCB approved laboratory and packing & stacking of dried sludge in the ETP vicinity is in the scope of contractor.


7.   SPECIFICATION OF ELECTRICAL WORKS : ( For Final Effluent  treatment plant)
7.1   Scope of Work :

A) 
Supply, installation and commissioning of electrical motors required for the process of      
    
  suitable capacity and approved make.
 B) 
Supply, installation and commissioning of Motor Control Center. 
C) 
Supply, installation and commissioning of any cabling required for remote  
control/interlocking purpose between vendors equipment and MCC, which includes  
control   cable if any.
D) Supply, laying, termination and commissioning of control cable of suitable size from  MCC to   push Button stations.
E) 
Supply, laying termination and commissioning of L T power cable of suitable sizes from  MCC to  all the motors and from MCC to main lighting distribution board.
E) Supply, installation and commissioning of required no, of push buttons stations to be located  near all the motors as per the chief Electrical Inspectorate Government of   Andhra Pradesh.
G)
Lighting of pump house at Effluent treatment plant only which consists of the following:

a)  Supply, fixing and commissioning of  3 phases 4 ways 32 amp, MCB distribution of      approved make i.e.,. incomer 32 amp.
b)  5amp. Plug point - 2 Nos. and 15 A plug point - 2 nos. with sockets/switch boxes.
c) Totally 10 nos. of Fluorescent tube light fittings with dual tube lights shall be considered. 

Necessary cablings and poles for outside are also in the scope of the contractor.

Complete wiring with suitable wire for the above pump house works to be done by the contractor. i.e. from main distribution board to light point/power points, including switches and switch boards. Necessary power supply for the plant operation will be provided by BHEL-Hyderabad at plant room only.
Earthing of all motors, MCC. Push buttons, main lightning DB and light points/power point etc. is included in scope of contractor.
The following guidelines shall be used for earthing.

For MCC  




- GI flat 25x 6mm

For motors up to 10 HP & PB stations and main lighting DB 
- GI 8 gauge

For motors above 10 HP





- 25 x 3 mm GI flat

For main lighting DB to light points/power points 


-2.5 sq.mm copper wire. 

Construction of masonry work chamber for two earth pits with GI covers.

Approval from the chief Electrical Inspector/Local EB authorities if required to be obtained by bidder. However, any statutory fees paid shall be reimbursed against submission of documentary (Proof including preparation and submission of drawing).

Sufficient length of rubber mats for MCC, Danger Board and 2 no. shock treatment charts. All externally mounted electric motor and reduction gears should be provided with weather shelf for protection from taint. 
Details to be furnished by contractor:

Exact ratings of all electrical loads in HP and KW and Total power requirement shall be indicated. The number of the feeders with rating to be furnished so that power supply arrangement could be made.
The contractor shall submit the following to the client for approval during engineering of contract.
i)    A Schedule giving details of all motors.

ii)  Single line diagram of MCC giving details of ratings of equipment like bus bar, Switch fuses, contractors, thermal relays etc., cable sizes etc., MCC drawing also to be submitted for approval.

 iii) A wiring Diagram showing: Terminal Nos. for connection for interconnecting cables at items of equipment's.
Schematic diagram showing inter looking sequence and control schemes, complete lighting layout showing the single line diagram.

7.2   Exclusions:

The main incoming power cable to the total project shall be terminated at one point  only  by BHEL. Further distribution shall be  done by the contractor.

7.3   MCC Panel:

MCC panel shall provide power supply to various connected electrical installations and shall also include control circuits for operation of the equipment's as detailed under:
The MCC shall be compartmentalized self standing with bottom cable entry and cable alley arrangements. The panel shall be fabricated from CRCS sheets of not less than 16 SWG. The angle frame structure shall be provided for sturdiness.
The MCC shall have two incomers interlocked MCCBs ( 4 poles) , out going feeders, controlled circuits etc. The rating of various components of the MCC shall be based on the connected load to be provided by the supplier.

The MCC shall have base frame fabricated from 75 x 40 M.S. channels. The compartment door should have interlock with switch in such a way that it can open only when the switch is in off position. The door should have flexible connections to the frame for earthing. The panel shall have earth bus running for full length of the panel. The panel shall be earthed at 2 places. The panel shall be epoxy painted with zinc rich epoxy primer 
of not less than 100 micron. The panel shall include level controllers. However the level controllers excluding sensor can be mounted in a separate panel fabricated for CRCS sheet of SWG with wall mounting arrangement. The sensor should be float operated. The sheet and the counter shall be of SS 316 and shall move inside HDPE pipe. The level indicator shall be calibrated from the depth of the sump/tank. It shall be possible to stop the drive from push button stations located nearer each pump. The inscription of each feeder shall be as per approved drawing.

Each pump which are located outside the pump house shall be provided with rain hood.

Paint shade shall be shade 631 of IS:5. Enclosure protection class shall be IP54 for MCC panel and for PB station it shall be IP 55.
The incomers shall be provided with voltmeter with selector switch and ammeter with selector switch & 3 phase energy meter. The individual feeders shall be provided with switch fuse unit, contactors, thermal overload relays, on /off/ trip push buttons & indicating lamps.
7.4  CABLING:
The cabling shall be by means of armored cable of suitable sizes. The minimum size for the power cable shall be 4 sq. mm aluminum or 1.5 sq. mm copper and all control shall be based on continuous current rating and also voltage drop shall be limited to 2.5%. Their termination shall be by means of lugs of approximate size BI metallic lugs should be used where ever 2 different types of metal are involved at the junction. No intermediate cable joint shall be permitted unless route length exceeds 500 Mts.
Cable indicates connections between MCC panel, local start/stop push button stations / motors. Cables laid in trenches shall be provided with sand covering.

Only ISI approved make of cables shall be accepted with test certificates furnished. Cables crossing roads shall be provided with casing pipes with proper protection. The tentative outgoing feeders and ratings details are as given below.
PRIMARY AND SECONDARY TREATMENT

	Air Blowers
	2 HP
	1 No. + 1 spare feeder

	Surface Aerator
	7.5 HP
	 2 nos.

	Clarifier Mechanism
	1 HP
	 1 no + 1 spare feeder.

	 Sludge recirculation pump
	2 HP
	 2 nos.

	Raw effluent pumps
	15 HP
	 2 nos.


Note: These are indicative only. Actual rating are to be finalised by the tenderer based on the final design.

Plus 2 Nos. TPN switch fuse for auxiliary duties(1 No.63 amp, S.F and 1 No. 32 amp. S.F. for welding and lighting.).
The tenderer to provide the actual out going feeder details & single line diagram indicating pump rating and feeder ratings.
8.      DOCUMENTATION

	Document details
	Time schedule

	 Flow diagram of FETP, layout of FETP OGA, SLD, BOM, scheme of electrical panels, PB station. OGA of mechanical equipments data sheet of various mechanical .item and cable, pipes. Pump and fan characteristics data sheet. etc.,
	 With in 4 weeks after LOL

	Piping schedule. Cable schedule, routing, Lighting layout. Earthing  schedule etc.,
	With in 6 weeks after LOI,

	Test certificates of all electrical items, mechanical items, material test certificates.
	At least one week prior to inspection of the equipments at vendor's premise.

	O&M manual with catalogues, recommended list of spares.
	Along with equipment dispatch.

	As built drawings ( 1 RTF + 2 sets)
	  Before handing over equipment


8.1   The following documentation shall be submitted during execution as per schedule given below:

8.2    The number of sets to be furnished shall be six. Manufacturing clearance shall be given to supplier for individual equipment after the corresponding drawing is approved by BHEL .
8.3   Bill of material shall indicate the make of supplier. Phrases like "equivalent/ reputed" etc is not accepted. Correct make of the equipment shall be mentioned.
8.4  The drawing size shall be A3/A4/A2 and all other sizes will not be acceptable. The equipment dispatch  details and packing list shall be clearer so that all sub parts are identifiable by a label given by supplier.
8.5  All equipment drawings are to be submitted in 7 sets for approval and after they are approved manufacturing clearance shall be given for individual items. The supplier shall give inspection call along with internal test certificates 10 days prior to inspection & testing. The equipments are to be inspected by our Engineers before dispatch and only after getting clear dispatch instructions and equipment should be dispatched. 
8.6   The O&M manual shall broadly cover (a) Brief process, description and flow sheet, (b) Design parameters of flow and treated effluent characteristics. (c) Unit wise function and Number of description of plant start up procedure. (d) Equipment wise details operational instruction, maintenance procedure and (e) Analysis methods for relative parameters (based on standard method)
Figure-1

[image: image1.jpg]FIGURE -1

FINAL EFFLUENT TREATMENT PLANT AT FACIORY OUT LET.

RAW EFFLOENT
FROM PLANT

Raw EFFLUES
Ol TRAP HOLDING TAr
I

SCREUEN CAAMBER

~J

PRAMAR|

CLARIFIER

TREATED WATER. l
DISCHARGED T
DRAN
BT b3

SECONIARY
CLARIFIER

€
UNDER FLOW FROM
SUIDGE DRY ING BED
To RAW EFF LUENT SLUDGE DRIING BEPS
HOLDING TANK





Note:         Flow meter (electro Magnetic)

ANNEXURE - I       TOLERANCE LIMITS FOR FINAL ETP

General Standards for Discharge of Environment Pollutants
(Ref: Schedule – VI Environmental (Protection) Rules’1986)

(All parameters except pH are in mg/L)

	S.No.
	Parameter
	Inland Surface Water

	1.
	Oil & Grease
	10

	2.
	Suspended Solids
	100

	3.
	pH                       
	5.5 - 9.0

	4.
	BOD
	30

	5.
	COD
	250

	6.
	Sulphide                 
	2.0

	7.
	Dissolved Phosphate
	5.0

	8.
	Nitrate                  
	10

	9.
	Fluoride                 
	2.0

	10.
	Manganese
	2

	11.
	Vanadium
	0.2

	12.
	Iron                     
	3

	13.
	Phenols                  
	1.0

	14.
	Cyanide                  
	0.2

	15.
	Arsenic                  
	0.2

	16.
	Cadmium                  
	2.0

	17.
	Hexavalent Chromium      
	0.1

	18.
	Total Chromium
	2.0

	19.
	Copper                   
	3.0

	20.
	Mercury
	0.01

	21.
	Lead                     
	0.1

	22.
	Zinc                     
	5.0

	23.
	Nickel
	3.0

	24.
	Selenium
	0.05

	25.
	Total Residual Chlorine
	1.0

	26.
	Ammonical Nitrogen
	50

	27.
	Total Kjeldahl Nitrogen
	100

	28.
	Free Ammonia
	50


ANNEXURE -2  :  LIST OF RELEVANT CODES AND STANDARDS:

	Sl.no
	Indian standards No.
	Description

	1
	IS: 456-1978 REV 3
	Code of Practice for plain and reinforced

	
	AMEMD2
	concrete (second division)

	2
	IS : 3370
	Code of Practice for concrete structures of

	
	
	the storage of liquids.

	
	Part I - 1965
	General requirements

	
	Part II - 1965
	Reinforced Concrete

	
	Part 111- 1967
	Pre stressed concrete structures.

	
	Part IV- 1967
	Design Tables

	3.
	IS: 1536-1989
	Centrifugal cast(spun) iron pressure pipes

	
	
	for water, gas & sewage.

	4
	IS: 1537 -1976
	Vertically cast iron pressure pipes for water,

	
	
	gas and sewage.

	5
	IS: 1538-1993
	Cast Iron fittings for pressure pipes for

	
	
	water, gas and sewage.

	6
	IS : 3114 - 1994
	Code for practice for laying of CI pipes.

	7.
	IS : 782-1978
	Caulking Lead.

	8.
	IS : 7634 - 1975 part II
	code of practice for laying and jointing of high density

	
	
	polyethylene pipes.

	9
	IS : 5639 - 1970
	Pumps handling chemicals & corrosive

	
	
	liquids.

	10
	IS: 2685 -1971
	Code of practice for selection, installation and

	
	
	maintenance of sluice valves.



BHARAT HEAVY ELECTRICALS LIMITED

HYDERABAD

TECHNICAL SPECIFICATIONS OF

 EFFLUENT TREATMENT PLANT BLOCK 08
INDEX

	SL.NO
	DESCRIPTION
	
	PAGE NO.

	1
	INTRODUCTION
	2

	2
	PRESENT STATUS
	3

	3
	BASIC DATA
	4

	4
	SCOPE OF WORK 
	5

	5
	PROPOSED SCHEME OF CONTRACT
	6

	6
	SIZES AND SPECIFICATIONS OF VARIOUS UNITS (CIVIL, ELECTRICAL &MECHANICAL WORKS)
	7

	7
	SPECIFICATION OF ELECTRICAL WORKS
	20

	8
	DOCUMENTATION
	
	25

	ANNEXURE
	
	
	

	1
	 ETP SCHEMATIC LAYOUT (FIGURE-1)
	26

	2
	TOLERANCE LIMITS FOR DISCHARGE FROM ETP (ANNEXURE-1)
	27

	3
	 LIST OF RELEVANT CODES & STANDARDS (ANNEXURE-2)
	28


~

Deviations from the specifications if any, shall be clearly brought out by the bidder with sufficient explanation separately at the end, giving reference to the clause number in the specification. Otherwise it will be presumed that the tender in total conformity is accepted by the bidder.
EFFLUENT TREATMENT PLANT - BLOCK 08
1. 
INTRODUCTION.

The BHEL Hyderabad unit was set up in 1963 and started its operations with manufacture of Turbo-generator sets and auxiliaries for 60 and 110 MW thermal utility sets. Over the years it has increased its capacity range and diversified its operations to many other areas. 

The factory is situated at Ramchandrapuram, approximately 23Km.  from Secundrabad Railway Station. At present there are about 6000 employees working in the plant. The township is situated adjacent to the factory having population of approximately 30,000 with about 4600 staff quarters. 

The manufacturing facilities at BHEL, Hyderabad include:

xi. TC&GT  - Block-01

xii. Electrical Machines – Block-02

xiii. Switch Gear Block-03

xiv. Foundry & Pattern shop – Blocks -04,05&09

xv. Heat Exchanger/Fabrication-Block-06

xvi. Tool Room Block-07

xvii. Heat Treatment and common work shop –Block-08

xviii. Pump manufacturing block –70

xix. Bowl Mill & Oil field Equipment – Block –51

xx. Services Department

· Transport

· Compressor House

· Producer Gas Plant

· Boiler House

· Diesel Power House 

· Canteens
· Oxygen plant

While manufacturing the above products, Industrial Effluent is being generated per day and is being sent for treatment at Sewage Treatment and Disposal Plant (STDP) along with domestic effluent.. This treatment plant is situated  5 Km away from BHEL Township. This plant also treats the sewage coming from BHEL township and adjoining colonies.Being an Engineering industry, pollution may be due to oil spillage and solid waste generated. Certain blocks like  block 08 and 03 block where metal coating and surface cleaning operation take place,  effluent containing metals, cyanide etc. are generated. Besides service areas like Producer gas plant,  Boiler house etc., generate process specific waste.

Job from various sections of the plant like Gas Turbine manufacturing shop, Pumps manufacturing shop , Fabrication area and Switch gears are brought to Block -08 for surface treatment. Three type of process take place in the shop

1. Electroplating

2. Stamping, Die pressing, Grinding, Hot and Cold bending

3. Heat treatment

In The electroplating process jobs are plated with hard chrome, nickel, tin, Zinc, cadmium, silver. Surface treatment process like anodisin, degreasing, pickling, phosphating and babbitting also takes place. 

In the forge shop within this block, jobs are Die stamped, Pressed, hot and cold bent and straightened.

Tempering, annealing of jobs along with hardening, nitrating and carburizing are done in the heat treatment shop. 

During the above activities water is consumed and effluent is generated containing metals and toxic substances like Cyanide. 

3. PRESENT STATUS

The effluents from Block-08  consists of Acids, Alkalis, Cyanides, Hexavalent Chromium and metals like Cadmium, Lead, Copper, Nickel and Silver. The total quantity of the effluent is around 5 m3/day, out of which chromium bearing effluent is 3 m3/day and Cyanide bearing effluent is 2 m3/day.

The chromium bearing effluent and Cyanide bearing effluent are separately collected from exclusively maintained Cyanide and Chromic acid lines in 5 m3/day capacity tanks. Depending on the concentration of Chromium and Cyanide, chemicals are added to reduce Cr+6 to Cr+3 and oxidize Cyanide to CO2 and N2. The treated effluents are then collected in a tank for neutralization and then sent to solar evaporation pond. 

3.            BASIC DATA: 

The basic data considered for preparing schematics and sizing of unit operations of effluent treatment plant are given below:
a)   Total effluent quantity: 5 m3 / day 

· Effluent containing  Chromium: 3 m3 / day

· Effluent containing Cyanide: 2 m3 / day   
b)  Characteristics of raw effluent: The characteristics of the effluent considered for designing the treatment for Block – 08 effluent are as given in table below:

TABLE: CHARACTERISTICS OF RAW EFFLUENT

	Sr. No.
	Parameter
	Concentration*

	1
	Chromium hexavalent
	56.0

	2
	Cyanide
	7.0


*All parameters expressed in mg/l

c)  Characteristics of treated effluent: The expected characteristics of the treated effluent on adopting the scheme of treatment given in  S.N. 5 are given in table below:

TABLE: CHARACTERISTICS OF TREATED EFFLUENT

	Sr. No.
	Parameter
	Concentration*



	1
	Chromium hexavalent
	< 0.1

	2
	Cyanide
	< 0.2


 *All parameters expressed in mg/l
4.0         SCOPE OF CONTRACT

Scope of work shall broadly include design, construction, erection & commissioning of effluent treatment plant  for  Block -08 & operating the plant for a period of 2 years  as per conceptual design and specifications given in Figure - 2. The tenderer should give the treated effluent quality confirming with the Andhra Pradesh State Pollution Board Standards (consent condition), as well as the parameters specified in Schedule VI of Environmental Protection rules 1986 (annexure-1) 

The following items are included with in the scope of work :

a)  All the civil works and structural fabrication works of the treatment plant as per the detailed description of the civil works and generally as per the scheme provided. Detailed drawings with tentative levels of individual structure are also to be prepared. The contactor shall get the detailed civil and Engineering drawing approved by BHEL prior to initiation of civil work at site.  Proposed scheme of the treatment plant of Block – 08 is enclosed in Figure- 2. The sizing and specifications given below (S.N. 6 & 7 ) are indicative only. The tenderer may cross check the sizing/broad specifications and modify, if required, to meet the quality of treated effluent. 
b)  Supply, erection and commissioning of all the equipments required for the treatment plants as per the individual equipment's specifications and details given herewith.

e) The scope of work includes all necessary civil works, like construction of MCC / control panel room, panel foundation, cable trenches cable supports, pipe supports, lighting of panel room etc. complete. The scope of work also includes in providing the puddle insert drawings as required for each unit operation of the Treatment Plant as per the envisaged scheme & layout plan.

d)  The scope of work also includes de-linking the existing effluent lines, and connecting the drain to the proposed Effluent treatment plant and re-linking the final treated discharge line to the Main drain. The agency has to inspect the site to ensure the invert level of the inlet pipe near the ETP site and also treated water receiving drain.

e) Obtaining all necessary statutory approvals from Andhra Pradesh State Pollution Control Board and other statutory bodies for construction and commissioning are included in the scope of work of contractor.

f)   The Horse Power (HP) of all the pumps, blower etc. shown are indicative. The actual HP shall be furnished by the contractor to meet the specified flow and head.

g)   Documentation shall be furnished as per clause 8.0.

h)  All temporary sheds, offices, go downs etc., required for storage of materials and for contractors supervisory personnel at site is the scope of the bidder. The required equipments and materials are to received and stored by the bidder and to be issued as and when needed for installation.

i)  Other general terms and conditions as applicable for similar contracts for Civil, Mechanical and Electrical  work at BHEL, Hyderabad

j)  All materials required for civil works & structural/fabrication works  (Cement, steel,  paints & structural steels etc.)  included in the vendors scope. However cement and steel will be issued by BHEL on cost recovery basis.

k)  BHEL will provide Electric power & Water at free of cost. The agency should make necessary arrangement for tapping from the approved source.
5.0      PROPOSED SCHEME OF TREATMENT:
Chromium bearing effluents are collected in a holding tank from where it will be  pumped to the chromium reduction tank with agitator. The pH will be adjusted by addition of sulphuric acid and required quantity of sodium bisulphite will be added. The effluent will be agitated to ensure proper mixing of chemicals and reduction of hexavalent chromium to its trivalent form.  From chromium reduction tank the waste water will be pumped into the neutralisation tank and sodium hydroxide will be added to raise the pH to 8.5 and precipitate the metal hydroxides. Effluent from acid/alkali rinse baths should be properly neutralized along with chromium effluent in the neutralization tank. In the chromium reduction tank and neutralization tank agitators will be provided for mixing of chemicals and waste water. From the neutralization tank the wastewater will be sent to  settling tank for solid – liquid separation. Suitable polyelectrolyte solution will be dosed and the effluent will be agitated for solid – liquid separation. The sludge collected at the  bottom of the settling tank will be periodically withdrawn and will be applied on sludge drying beds for dewatering and drying. Underflow from the sludge drying beds will be sent back to the holding tank. Overflow from the settling tank will be  discharged in the main drain. The proposed treatment scheme is shown in Figure- 2. Though not shown in the layout scheme, Plant bye pass shall be ensured in the event of maintenance.

     The cyanide bearing effluents will be collected in a holding tank from where it will be  pumped to the cyanide oxidation tank I. The cyanides will be oxidized to cyanates in the first stage oxidation tank. For the chemical reaction to take place and to maintain the pH, required quantity of NaOCl and NaOH will be dosed. From the 1st stage oxidation tank the wastewater will be  taken to 2nd stage oxidation tank to oxidize the cyanates to CO2 and N2. For the chemical reaction to take place NaOCl and NaOH will again be dosed in required quantities. In both the tanks agitators will be provided for mixing of chemicals and wastewater. Following the oxidation the effluent will be  led to the settling tank for solid liquid separation. The sludge collected at the bottom of the settling tank will be periodically withdrawn and will be applied on sludge drying beds for dewatering and drying. Underflow from the sludge drying beds will be led back to the cyanide effluent holding tank. Overflow from the settling tank will be discharged in the main drain. The proposed treatment scheme is shown in    Figure-2. Though not shown in the layout scheme, Plant bye pass shall be ensured in the event of maintenance.
6.0        SIZES AND SPECIFICATIONS OF VARIOUS UNITS (CIVIL, ELECTRICAL AND     MECHANICAL WORKS) FOR THE PROPOSED PLANT.

6.1  Civil Works:

Specification Table  No. 6.1.1
	UNIT
	CHROMIUM EFFLUENT HOLDING TANK

	Duty
	To hold effluent with chromium for pumping

	Number of Units
	One

	Size
	2.5 m X 2.5 m X 1.0 m SWD

	MOC
	RCC M-25 with epoxy coating


Specification Table  No. 6.1.2
	UNIT
	CYANIDE EFFLUENT HOLDING TANK

	Duty
	To hold effluent with cyanide for pumping

	Number of Units
	One

	Size
	2.5 m X 2.5 m X 1.0 m SWD

	MOC
	RCC M-25 with epoxy coating


Specification Table  No. 6.1.3
	UNIT
	CHROMIUM REDUCTION TANK 

	Duty
	To reduce hexavalent chromium to its trivalent form.

	Number of Units
	One

	Size
	2.5 m X 2 m X 1.5 m SWD +0.5 m FB

	MOC
	RCC M-25 with epoxy coating


Specification Table  No. 6.1.4
	UNIT
	NEUTRALISATION TANK 

	Duty
	To neutralize the wastewater 

	Number of Units
	One

	Size
	2.5 m X 2 m X 1.5 m SWD + 0.5 m FB

	MOC
	RCC M-25 with epoxy coating


Specification Table  No. 6.1.5
	UNIT
	CYANIDE OXIDATION TANK - I  

	Duty
	To oxidise cyanide in the wastewater.

	Number of Units
	One

	Size
	2.5 m X 2 m X 1.5 m SWD + 0.5 m FB

	MOC
	RCC M-25 with epoxy coating


Specification Table  No. 6.1.6
	UNIT
	CYANIDE OXIDATION TANK - II  

	Duty
	To oxidise cyanide in the wastewater.

	Number of Units
	One

	Size
	2.5 m X 2 m X 1.5 m SWD + 0.5 m FB

	MOC
	RCC M-25 with epoxy coating


Specification Table No.6.1.7

	UNIT
	SETTLING TANK

	Duty
	To enable solid liquid separation 

	No. of units
	Two (one for chromium effluent  and one for cyanide effluent)

	Size          
	1.8 m X 1.8 m X 2.5 m SWD + 0.5 m FB with a bottom slope and channel for collection of sludge.

	MOC
	RCC M-20


Specification Table  No. 6.1.8
	UNIT
	SLUDGE DRYING BEDS

	Duty
	For dewatering and drying of sludge.

	Number of Units
	Two (As cyanide treatment would hardly   generate any sludge, one sludge drying bed would be used  for both chromium and cyanide treatment processes.) to be used alternately.

	Size
	3.0 m X 2.0 m X 0.8 m each

	MOC
	Base in PCC and walls in brick work.


6.2   Mechanical works:
Specification Table No. : 6.2.1

	UNIT
	PUMPS

	Duty


	 To pump wastewater for onward treatment from chromium effluent holding tank and cyanide effluent holding tank

	No. of units 


	 Four ( two for each stream 50 % standby )

	Capacity


	2.0 cum/hr. 

	Head


	 10 m.

	Type


	 Non clog, self priming centrifugal pumps. 


Specification Table No. : 6.2.2

	UNIT
	AGITATOR

	Duty

	To mix chemicals and wastewater for treatment viz.  Chromium  reduction tank, Neutralization tank,  CN oxidation tank I and II.

	No. of units 

	 Four  

	Rating                           
	 2.0 HP

	Type 
	Slow speed paddle type

	MOC
	Shaft & paddle in SS 316

	Drive


	Electric motor coupled to speed reduction gear box.


Specification Table No. : 6.2.3

	UNIT
	SULPHURIC ACID TANK

	Duty

	To hold sulphuric acid

	No. of units 

	 One  

	Volume                             
	 250 liters

	MOC


	 HDPE


Specification Table No. : 6.2.4

	UNIT
	SODIUM  BISULPHITE TANK 

	Duty

	To hold sodium bisulphite solution

	No. of units 

	 One  

	Volume                             
	 250 liters

	MOC


	 HDPE


Specification Table No. : 6.2.5

	UNIT
	POLYELECTROLYTE TANK 

	Duty

	To hold Polyelectrolyte

	No. of units 

	 One  

	Volume                             
	 50 liters

	MOC


	 HDPE


Specification Table No. : 6.2.6

	UNIT
	SODIUM HYDROXIDE TANK 

	Duty

	To hold sodium hydroxide solution

	No. of units 

	 Two,  one for neutralization tank of Chromium treatment and one for oxidation tank of CN treatment 

	Volume                             
	 250 liters

	MOC


	 HDPE


Specification Table No. : 6.2.7

	UNIT
	SODIUM HYPOCHLORITE TANK 

	Duty

	To hold sodium hypochlorite solution

	No. of units 

	 One  

	Volume                             
	 250 liters

	MOC


	 HDPE


Specification Table No. : 6.2.8

	UNIT
	AGITATOR

	Duty

	To enable preparation of chemical solutions

	No. of units 

	 Four (one for Sodium Bi-sulphite, NaOH in Chromium treatment and Sodium Hypochlorite, NaOH in Cyanide treatment) 

	Rating                           
	 1.0 HP

	Type 
	Slow speed paddle type

	MOC
	Shaft & paddle in SS 316

	Drive


	Electric motor coupled to speed reduction gear box.


Specification Table No. 6.2.9

	UNIT
	SULPHURIC ACID DOSING PUMP

	Duty
	To dose sulphuric acid in a regulated manner

	Number of Units
	Two (1 working +1 standby)

	Capacity                    
	0-6 lph each @ 5 m head  

	Type            
	Electronic variable dosing

	Make
	e- dose, Etatron or equivalent


Specification Table No. 6.2.10

	UNIT
	SODIUM BISULPHITE DOSING PUMP

	Duty
	To dose sodium bi-sulphite in a regulated manner

	Number of Units
	Two (1 working +1 standby)

	Capacity                    
	0-6 LPH each @ 5 m head  

	Type            
	Electronic variable dosing

	Make
	e- dose, Etatron or equivalent


Specification Table No. 6.2.11

	UNIT
	POLYELECTROLYTE DOSING PUMP

	Duty
	To dose polyelectrolyte in a regulated manner

	Number of Units
	Two (1 working +1 standby)

	Capacity                    
	0-6 LPH each @ 5 m head  

	Type            
	Electronic variable dosing

	Make
	e- dose, Etatron or equivalent


Specification Table No. 6.2.12

	UNIT
	SODIUM HYDROXIDE DOSING PUMP

	Duty
	To dose sodium hydroxide in a regulated manner

	Number of Units
	Two (1 working +1 standby)

	Capacity                    
	0-6 LPHeach @ 5 m head  

	Type            
	Electronic variable dosing

	Make
	e- dose, Etatron or equivalent


Specification Table No. 6.2.13

	UNIT
	SODIUM HYPOCHLORITE DOSING PUMP

	Duty
	To dose sodium hydroxide in a regulated manner

	Number of Units
	Two (1 working +1 standby)

	Capacity                    
	0-6 lph each @ 5 m head  

	Type            
	Electronic variable dosing

	Make
	e- dose, Etatron or equivalent


Specification Table No. 6.2.14

	UNIT
	RATE OR FLOW METER

	Duty
	To measure flow of effluent

	Number of Units
	One

	Capacity                    
	Suitable flow meter (Electro Magnetic) to measure instantaneous and cumulative flow with digital display. (0-700 KLD). Make Forbes marshalL/Endress & Hauser


Specification Table No. : 6.2.15

	UNIT
	CONTROL PANNEL

	Duty
	For operation and protection of all electrical starters.

	Incoming
	MCCB of adequate rating, ammeter, voltmeter, copper bus bar and phase indicating lamps.

	Out going
	Contactors of suitable rating of DOL type for motor rating up to 10 HP and Star-Delta type for motor ratings above 10 HP, thermal overload relay with built-in single phase preventer and HRC fuses for extra protection.

	Make
	All electrical items shall be of L&T, English Electric, GEC, Crompton, IMP,MECO or Siemens.

Separate panels shall be provided for each of the streams being fed to the RO

	Electrical cabling 


	All interconnecting cabling within ETP shall be in PVC insulated, armored /unarmored, aluminum conductor of standard make. Cabling, as far as practicable, shall be underground.


Specification Table No. : 6.2.16

	UNIT
	INTERCONNECTING PIPING AND VALVES

	Duty
	Interconnection     between    the various units of the STP.

	Type


	a)  Piping : Generally all  piping shall  be in HDPE/PVC/GI/CI and of suitable size & pressure rating. 

b)  All   valves   shall   be  of  polypropylene/CI/GM


Specification Table No. 6.2.17

	UNIT
	ERECTION & COMMISSIONING

	Duty
	To erect the effluent treatment plant. After erection of the effluent treatment plant, the entire plant shall be commissioned to obtain the desired results. An operation and maintenance manual (3 copies) shall also be provided to the client. Necessary approval / clearance shall be obtained from the statutory authorities.


Specification Table No. 6.2.18

	UNIT
	OPERATION & MAINTENANCE

	Duty
	The effluent treatment plant has to be operated and maintained for a period of 24 months after obtaining the desired results / approval from the statutory authorities. All consumables, treatment chemicals, labour, repair and maintenance for regular running of the effluent treatment plant shall have to be borne by the tenderer. Periodical monitoring of treated effluents from PCB approved laboratory and packing & stacking of dried sludge in the ETP vicinity is in the scope of contractor


Specification Table No. 6.2.19

	UNIT
	INTERCONNECTING PIPING AND VALVES

	SI.

No.
	From
	To
	Size
	Material
	Valves

	
	
	
	mm
	
	

	
	CHROMIUM TREATMENT
	
	
	
	

	1
	Chromium Holding Tank
	Chromium Reduction Tank
	150 Dia
	HDPE
	-

	2
	Chromium Reduction Tank
	Neutralization
	150 Dia
	HDPE
	1 no. 125 mm

sluice valve

	3
	Neutralization Tank
	Settling Tank
	150 Dia
	HDPE
	1 no. 125 mm

sluice valve

	4
	Settling Tank
	Sludge drying bed
	150 Dia
	HDPE
	1 no. 125 mm

sluice valve

	5
	Sludge drying bed filtrate
	Chromium Reduction Tank
	150 Dia
	HDPE
	1 no. 125 mm

sluice valve

	6
	Settling Tank over flow
	Plant drain
	150 Dia
	HDPE
	-

	7
	Sulphuric Acid Tank 
	Chromium Reduction Tank
	100 Dia
	    HDPE
	-

	8
	Sodium Sulphite Tank
	Chromium Reduction Tank
	100 Dia
	HDPE
	-

	9
	NaOH Tank
	Neutralisation Tank
	100 Dia
	HDPE
	-

	10
	Poly-electrolyte Tank
	Neutralisation Tank
	100 Dia
	HDPE
	-


	
	CYANIDE TREATMENT
	
	
	
	

	1
	Cyanide Holding Tank 
	Cyanide Oxidation Tank
	150 Dia
	HDPE
	-

	2
	Cyanide Oxidation Tank
	Settling Tank
	150 Dia
	HDPE
	1 no.125 mm

sluice valve

	3
	Settling Tank
	Sludge drying bed
	150 Dia
	HDPE
	1 no. 125 mm

sluice valve

	4
	Settling Tank over flow
	Plant drain
	150 Dia
	HDPE
	-

	
	
	
	
	
	

	5
	Sludge drying beds

Filtrate
	Cyanide Holding Tank
	150 Dia
	HDPE
	1 no.125 mm

sluice valve

	6
	NaOCl Tank
	Cyanide Oxidation Tank
	100 Dia
	HDPE
	1 no.  stop valve for CN Tank-I

	7
	NaOH Tank
	Cyanide Oxidation Tank
	100 Dia
	HDPE
	1 no. stop valve for CN Tank -II


Note:

1)   Sluice valves should be of HDPE.

2)   The above quantity and size specified are indicative only. Tenderer shall access and quote for the correct quantity and size indicating the requirement as per schematic diagram given in Figure-2.

3) Necessary Pipe & Valve as indicated in the plan to be provided for by-passing each unit in case of its cleaning in the scope of work.

7.   SPECIFICATION OF ELECTRICAL WORKS: (Block - 08 Effluent treatment plant)

7.1   Scope of Work :

A) 
Supply, installation and commissioning of electrical motors required for the process of      

    
  suitable capacity and approved make.

 B) 
Supply, installation and commissioning of Motor Control Center. 

C) 
Supply, installation and commissioning of any cabling required for remote control/interlocking purpose between vendors equipment and MCC, which includes control   cable if any.

F) Supply, laying, termination and commissioning of control cable of suitable size from  MCC 

to   push Button stations.

E) 
Supply, laying termination and commissioning of L T power cable of suitable sizes from               MCC to  all the motors and from MCC to main lighting distribution board.

G) Supply, installation and commissioning of required no, of push buttons stations to be located  near all the motors as per the chief Electrical Inspectorate Government of   Andhra Pradesh.

G)
 Lighting of control house at Effluent treatment plant only which consists of the following:

a) Supply, fixing and commissioning of  phases 4 ways 32 amp, MCB distribution of  

    approved make i.e.,. incomer 32 amp.

b)  5amp. Plug point - 2 Nos. and 15 A plug point - 2 nos. with sockets/switch boxes

c) Suitable numbers of Fluorescent tube light fittings with dual tube lights shall be considered. 

Necessary cablings and poles for outside are also in the scope of the contractor.

Complete wiring with suitable wire for the above pump house works to be done by the contractor. i.e. from main distribution board to light point/power points, including switches and switch boards. Necessary power supply for the plant operation will be provided by BHEL-Hyderabad at plant room.

Earthing of all motors, MCC. Push buttons, main lightning DB and light points/power point etc. is included in scope.

The following guidelines shall be used for earthing.

For MCC  




 - GI flat 25x 6mm

For motors up to 10 HP & PB stations and main lighting DB 
 - GI 8 gauge

For motors above 10 HP





 - 25x 3 mm GI flat

For main lighting DB to light points/power points 


 

- 2..5 sq. mm copper wire. 

Construction of masonry work chamber for two earth pits with GI covers.

Approval from the chief Electrical Inspector/Local EB authorities if required to be obtained by bidder. However, any statutory fees paid shall be reimbursed against submission of documentary (Proof including preparation and submission of drawing).

Sufficient length of rubber mats for MCC, Danger Board and 2 no. shock treatment charts. All externally mounted electric motor and reduction gears should be provided with weather shelf for protection from taint. 

Details to be furnished by contractor:

Exact ratings of all electrical loads in HP and KW and Total power requirement shall be indicated. The number of the feeders with rating to be furnished so that power supply arrangement could be made.

The contractor shall submit the following to the client for approval during engineering of contract.

i)   A Schedule giving details of all motors.

ii)  Single line diagram of MCC giving details of ratings of equipment like bus bar, Switch fuses, contractors, thermal relays etc., cable sizes etc., MCC drawing also to be submitted for approval.

 iii)A wiring Diagram showing: Terminal Nos. for connection for interconnecting cables at items of equipment's.

Schematic diagram showing inter looking sequence and control schemes, complete lighting layout showing the single line diagram.

7.2   Exclusions:

The main incoming power cable to MCC for the Effluent plant shall be in the purchaser's scope .

7.3   MCC Panel:

MCC panel shall provide power supply to various connected electrical installations and shall also include control circuits for operation of the equipment's as detailed under:

The MCC shall be compartmentalized self standing with bottom cable entry and cable alley arrangements. The panel shall be fabricated from CRCS sheets of not less than 16 SWG. The angle frame structure shall be provided for sturdiness.

The MCC shall have two incomers interlocked MCCBs ( 4 poles) , out going feeders, controlled circuits etc. The rating of various components of the MCC shall be based on the connected load to be provided by the supplier.

The MCC shall have base frame fabricated from 75x40 M.S. channels. The compartment door should have interlock with switch in such a way that it can open only when the switch is in off position. The door should have flexible connections to the frame for earthing. The panel shall have earth bus running for full length of the panel. The panel shall be earthed at 2 places. The panel shall be epoxy painted with zinc rich epoxy primer of not less than 100 micron. The panel shall include level controllers. However the level controllers excluding sensor can be mounted in a separate panel fabricated for CRCS sheet of SWG with wall mounting arrangement. The sensor should be float operated. The sheet and the counter shall be of SS 316 and shall move inside HOPE pipe. The level indicator shall be calibrated from the depth of the sump/tank. It shall be possible to stop the drive from push button stations located nearer each pump. The inscription of each feeder shall be as per approved drawing.

Each pump which are located outside the pump house shall be provided with rain hood.

Paint shade shall be shade 631 of IS:5. Enclosure protection class shall be IP54 for MCC panel and for PB station it shall be IP 55.

The incomers shall be provided with voltmeter with selector switch and ammeter with selector switch & 3 phase energy meter. The individual feeders shall be provided with switch fuse unit, contactors, thermal overload relays, on /off/ trip push buttons & indicating lamps.

7.4  CABLING:

The cabling shall be by means of armored cable of suitable sizes. The minimum size for the power cable shall be 4 sq. mm aluminum or 1.5 sq. mm copper and all control shall be based on continuous current rating and also voltage drop shall be limited to 2.5%. Their termination shall be by means of lugs of approximate size BI metallic lugs should be used where ever 2 different types of metal are involved at the junction. No intermediate cable joint shall be permitted unless route length exceeds 500 Mts.

Cable indicates connections between MCC panel, local start/stop push button stations / motors. Cables laid in trenches shall be provided with sand covering.

Only ISI approved make of cables shall be accepted with test certificates furnished. Cables crossing roads shall be provided with casing pipes with proper protection. The tentative outgoing feeders and ratings details are as given below.

	Recirculation Pump for CRT
	1 HP
	1 No. + 1 spare feeder

	Recirculation Pump for COT
	1 HP
	1 No. + 1 spare feeder

	NaOH Dosing Pump
	0.5 HP
	1 no + 1 spare feeder.

	Effluent Transfer pump
	2 HP
	2 nos.


Note: These are indicative only. Actual rating are to be finalised by the tenderer based on the final design
Plus 2 Nos. TPN switch fuse for auxiliary duties(1 No.63 amp, S.F and I No. 32 amp. S.F. for welding and lighting.).

The tenderer to provide the actual out going feeder details.& single line diagram indicating pump rating and feeder ratings.

General notes :

1. All internal surfaces shall be provided with 20mm thick smooth cement plaster with water proofing compound in CM 1:4 unless otherwise specified. All exposed surfaces above ground level shall be plastered with 20 mm thick sand plaster in 2 coats of 12 mm and 8 mm thick and all external surfaces will be painted with cement paint of approved make and shade. The flooring of the tanks shall be 40mm thick IPS flooring in PCC 1 :2:4 with necessary slope etc., complete. All the structure shall be water tight. All ground level and above ground level structures tanks shall be provided with hand rails and ladders as necessary to suit site conditions with MS pipes.

2.  Calibration chart indicating depth of Flow with Effluent Quantity to be provided.

3. All external surface would be suitably painted with cement paint of good quality. Colour will be finalized in consultation with BHEL, Hyderabad

4. Name plate to be displayed on each unit and an overall layout be separately displayed

8.   DOCUMENTATION

	Document details
	Time schedule

	Flow diagram of Block 08 ETP, layout of ETP OGA, SLD, BOM, scheme of electrical panels, PB station. OGA of mechanical equipments data sheet of various mechanical .item and cable, pipes. Pump and fan characteristics data sheet. etc.,
	 With in 4 weeks after LOL

	Piping schedule. Cable schedule, routing, Lighting layout. Earthing  schedule etc.,
	With in 6 weeks after LOI,

	Test certificates of all electrical items, mechanical items, material test certificates.
	Atleast one week prior to inspection of he equipments at vendor's premise.

	O&M manual with catalogues, recommended list of spares.
	Along with equipment dispatch.

	As built drawings ( 1 RTF + 7 sets)
	Before handing over equipment

	Chemical dosage for chromium and cyanide treatment
	Before handing over ETP

	Testing kit for analysis of Cyanide and Chromium
	Before handing over ETP


 8.1  The following documentation shall be submitted during execution as per schedule given :

8.2  The number of sets to be furnished shall be six. Manufacturing clearance shall be given to supplier for individual equipment after the corresponding drawing is approved by BHEL .

8.3   Bill of material shall indicate the make of supplier. Phrases like "equivalent/ reputed" etc is not accepted. Correct make of the equipment shall be mentioned.

8.4   The drawing size shall be A3/A4/A2 and all other sizes will not be acceptable. The equipment dispatch  details and packing list shall be clearer so that all sub parts are identifiable by a label given by supplier.

8.5   All equipment drawings are to be submitted in 7 sets for approval and after they are approved manufacturing clearance shall be given for individual items. The supplier shall give inspection call along with internal test certificates 10 days prior to inspection & testing. The equipments are to be inspected by our Engineers before dispatch and only after getting clear dispatch instructions and equipment should be dispatched. 

8.6   The O&M manual shall broadly cover (a) Brief process, description and flow sheet, (b) 

Design parameters of flow and treated effluent characteristics. (c) Unit wise function and Number of description of plant start up procedure. (d) Equipment wise details operational instruction, maintenance procedure and (e) Analysis methods for relative parameters (based on standard method).

Figure – 2

[image: image2.jpg]FiGURE-Z

[ | .
suLPe R ZooihM Bi-] Nlnulinl.n_ :;\.\ BLOCK-O8
W | |subeud, et crvouire
CAROMIUM o =
SEAE e
e & posiNG | DosiVG Pusp|
i | & o OVERFLOW FROM SETTLING
N d P> TANK IS DISCHARGED)
) T DRAIN.
* sl *G‘Tﬁf.? UNDER Flow FROM SLUDGE
SETTLING “TaNK, DRYING BED BAGK TO
CHRANIA REPUETION,
! o TANK
-
7 LOPES: CHANMEL AT
CHRO A NEUTRAL ZATION =
TANK BOTTOM FOR COLLEGTIN
REDUCTION  Sepywmineo <HLo|
TARK ZERWNINGO LRI & PISCHARGE oF stipas TTE—1
Naoel ey,
ALKALINE cYAMDE
BEARING EFFLUENT

FioM CNHOLDING TAMK
55N G

. o
=

7ir

o
SLUDGE DRYING
BEVS

£

VER FLOW
FROM SETTLING

TANK 1S DISCHAR-
GER To DRAIN,

i

UNDER FLOW FROM SLUDGE
DRYING BED BACK To
CYAMIDE EFF. HOLbING
TANK.

SETTLING TANK

OXIDATION | & XIDATION

SLOPE <& GHANNEL AT BoTTom
FOR GOLLECT 1M AND
DISCHARGE SF SLUDGE





ANNEXURE - I       TOLERANCE LIMITS FOR Discharge from ETP

General Standards for Discharge of Environment Pollutants

(Ref: Schedule – VI Environmental (Protection) Rules’1986)

(All parameters except pH are in mg/L)

	S.No.
	Parameter
	Inland Surface Water

	1.
	Oil & Grease
	10

	2.
	Suspended Solids
	100

	3.
	pH                       
	5.5 - 9.0

	4.
	BOD
	30

	5.
	COD
	250

	6.
	Sulphide                 
	2.0

	7.
	Dissolved Phosphate
	5.0

	8.
	Nitrate                  
	10

	9.
	Fluoride                 
	2.0

	10.
	Manganese
	2

	11.
	Vanadium
	0.2

	12.
	Iron                     
	3

	13.
	Phenols                  
	1.0

	14.
	Cyanide                  
	0.2

	15.
	Arsenic                  
	0.2

	16.
	Cadmium                  
	2.0

	17.
	Hexavalent Chromium      
	0.1

	18.
	Total Chromium
	2.0

	19.
	Copper                   
	3.0

	20.
	Mercury
	0.01

	21.
	Lead                     
	0.1

	22.
	Zinc                     
	5.0

	23.
	Nickel
	3.0

	24.
	Selenium
	0.05

	25.
	Total Residual Chlorine
	1.0

	26.
	Ammonical Nitrogen
	50

	27.
	Total Kjeldahl Nitrogen
	100

	28.
	Free Ammonia
	50


ANNEXURE 2 : LIST OF RELEVANT CODES AND STANDARDS:

	Sl.no
	Indian standards No.
	Description

	1
	IS: 456-1978 REV 3
	Code of Practice for plain and reinforced

	
	AMEMD2
	concrete (second division)

	2
	IS : 3370
	Code of Practice for concrete structures of

	
	
	the storage of liquids.

	
	Part I - 1965
	General requirements

	
	Part II - 1965
	Reinforced Concrete

	
	Part 111- 1967
	Pre stressed concrete structures.

	
	Part IV- 1967
	Design Tables

	3.
	IS: 1536-1989
	Centrifugal cast(spun) iron pressure pipes

	
	
	for water, gas & sewage.

	4
	IS: 1537 -1976
	Vertically cast iron pressure pipes for water,

	
	
	gas and sewage.

	5
	IS: 1538-1993
	Cast Iron fittings for pressure pipes for

	
	
	water, gas and sewage.

	6
	IS : 3114 - 1994
	Code for practice for laying of CI pipes.

	7.
	IS : 782-1978
	Caulking Lead.

	8.
	IS : 7634 - 1975 part II
	code of practice for laying and jointing of high density

	
	
	polyethylene pipes.

	9
	IS : 5639 - 1970
	Pumps handling chemicals & corrosive

	
	
	liquids.

	10
	IS: 2685 -1971
	Code of practice for selection, installation and

	
	
	maintenance of sluice valves.



~

BHARAT HEAVY ELECTRICALS LIMITED

HYDERABAD

TECHNICAL SPECIFICATIONS OF

 EFFLUENT TREATMENT PLANT – BLOCK 03
INDEX

	SL.NO
	DESCRIPTION
	
	PAGE NO.

	1
	INTRODUCTION
	2

	2
	PRESENT STATUS
	3

	3
	BASIC DATA
	4

	4
	SCOPE OF WORK 
	5

	5
	PROPOSED SCHEME OF CONTRACT
	7

	6
	SIZES AND SPECIFICATIONS OF VARIOUS UNITS (CIVIL, ELECTRICAL &MECHANICAL WORKS)
	7

	7
	SPECIFICATION OF ELECTRICAL WORKS
	16

	8
	DOCUMENTATION
	
	21

	ANNEXURE
	
	
	

	1
	 ETP SCHEMATIC LAYOUT (FIGURE-1)
	22

	2
	TOLERANCE LIMITS FOR DISCHARGE FROM ETP (ANNEXURE-1)
	23

	3
	 LIST OF RELEVANT CODES & STANDARDS (ANNEXURE-2)
	24


Deviations from the specifications if any, shall be clearly brought out by the bidder with sufficient explanation separately at the end, giving reference to the clause number in the specification. Otherwise it will be presumed that the tender in total conformity is accepted by the bidder.
EFFLUENT TREATMENT PLANT - BLOCK 03

1. 
INTRODUCTION.

The BHEL Hyderabad unit was set up in 1963 and started its operations with manufacture of Turbo-generator sets and auxiliaries for 60 and 110 MW thermal utility sets. Over the years it has increased its capacity range and diversified its operations to many other areas. 

The factory is situated at Ramchandrapuram, approximately 23Km.  from Secundrabad Railway Station. At present there are about 6000 employees working in the plant. The township is situated adjacent to the factory having population of approximately 30,000 with about 4600 staff quarters.

The manufacturing facilities at BHEL, Hyderabad include:

xxi. TC&GT  -Block-01

xxii. Electrical Machines - Block02

xxiii. Switch Gear and Breaker  Block-03

xxiv. Foundry & Pattern making shop – Block-04,05&09

xxv. Heat Exchanger/Fabrication-Block-06

xxvi. Tool Room Block-07

xxvii. Heat Treatment and common work shop –Block-08

xxviii. Pump manufacturing block –70

xxix. Bowl Mill & Oil field Equipment – Block –51

xxx. Services Department

· Transport

· Compressor House

· Producer Gas Plant

· Boiler House

· Diesel Power House

· Canteens

· Oxygen Plant

While manufacturing the above products, Industrial Effluent is being generated per day and is being sent for treatment at Sewage Treatment and Disposal Plant (STDP) along with domestic effluent.. This treatment plant is situated  5 Km away from BHEL Township. This plant also treats the sewage coming from BHEL Township and adjoining colonies.

Being an Engineering industry, pollution may be due to oil spillage and solid waste generated. Certain blocks like  block 08 and 03 block where metal coating and surface cleaning operation take place,  effluent containing metals, cyanide etc. are generated. Besides service areas like Producer gas plant, Boiler house etc., generate process specific waste.

Job from various sections of the plant like Gas Turbine manufacturing shop, Pumps manufacturing shop , Fabrication area and Switch gears are brought to Block -03 for surface treatment like pickling and phosphating. During the process the tank solution get contaminated with metals like Chromium, Copper and Nickel. 

Phosphating of the various jobs are also done  in this area. The saturated baths have to be refilled once in three months. This generates effluent with high phosphate content. 

During the above activities water is consumed and effluent is generated containing metals and toxic substances.

The rinse baths and the plating baths are discharged once in 3 months. The total quantity of effluent generated is around 6 KL in three months.

4. PRESENT STATUS

In Block-03, various jobs/parts are brought to this unit for pickling and surface treatment as also phosphating. The jobs are dipped into the respective baths and then rinsed in water. The treated jobs are sent to various blocks and the tank solution reused. Once in three month the rinse solution gets contaminated and has to be changed.  The total amount of effluent generated is around 6 KL in three months. The effluent is presently being stored in an underground RCC tank of size 2.74 m x 1.74 m x 2.28 m.  The effluent after being neutralized is discharged into the drain. The effluent has been found to contain Chromium and Copper levels higher than the stipulated values.

5. BASIC DATA: 

The basic data considered for preparing schemes and sizing of unit operations of effluent treatment plant are given below:

a)  Total effluent quantity: 6 m3 / 3 months. 

b) Characteristics of raw effluent: The characteristics of the effluent considered for designing, sizing of  the treatment plant for Block – 03 are as given in table below:

 TABLE: CHARACTERISTICS OF RAW EFFLUENT

	Sr. No.
	Parameter
	Concentration*

	1
	Chromium hexavalent
	3 - 5

	2
	Copper
	10 - 15 

	3
	Nickel 
	6 - 7 


*All parameters expressed in mg/l

c) Characteristics of treated wastewater: The expected characteristics of the treated effluent  on adopting the scheme of treatment given in  S.N. 5 are as given in table below:
TABLE: CHARACTERISTICS OF TREATED EFFLUENT 

	 Sr. No.
	Parameter
	Concentration*

	1
	Chromium hexavalent
	< 0.1

	2
	Copper
	< 3.0

	3
	Nickel
	< 3.0


 *All parameters expressed in mg/l

4. 
SCOPE OF CONTRACT

Scope of work shall broadly include design, construction, supply, erection and commissioning of Effluent treatment plant  for  Block -03  & operating the plant for a period of 2 years as per conceptual design and specifications given in Figure - 3. The tenderer should give the treated effluent quality confirming with the Andhra Pradesh State Pollution Board Standards (consent condition), as well as the parameters specified in Schedule VI of Environmental Protection rules 1986 (annexure-1).
The following items are included with in the scope of work :

a)  All the civil works and structural fabrication works of the treatment plant as per the detailed description of the civil works and generally as per the scheme provided. Detailed drawings with tentative levels of individual structure are also to be prepared. The contactor shall get the detailed civil and Engineering drawing approved by BHEL prior to initiation of civil work at site.  Proposed scheme of the treatment plant of Block – 03 is enclosed in Figure- 3. The sizing and specifications given below ( S.N. 6 & 7 ) are indicative only. The tenderer may cross check the sizing/broad specifications and modify, if required, to meet the quality of treated effluent. 

b)  Supply, erection and commissioning of all the equipments required for the treatment plants as per the individual equipment's specifications and details given herewith.

f) The scope of work includes all necessary civil works, like construction of MCC / control panel room, panel foundation, cable trenches cable supports, pipe supports, lighting of panel room etc. complete. The scope of work also includes in providing the puddle insert drawings as required for each unit operation of the Treatment Plant as per the envisaged scheme & layout plan.

d)  The scope of work also includes de-linking the existing effluent lines, and connecting the drain to the proposed efluent treatment plant and re-linking the treated discharge line to the Main drain. The agency has to inspect the site to ensure the invert level of the inlet pipe near the ETP site and also treated water receiving drain.

e)  Obtaining all necessary statutory approvals from Andhra Pradesh State Pollution Control Board and other statutory bodies for construction and commissioning are included in the scope of work of contractor.

f)   The Horse Power (HP) of all the pumps, blower etc. shown are indicative. The actual HP shall be furnished by the contractor to meet the specified flow and head.

g)   Documentation shall be furnished as per clause 8.0

h) All temporary sheds, offices, go downs etc., required for storage of materials and for contractors supervisory personnel at site is the scope of the bidder. The required equipments and materials are to received and stored by the bidder and to be issued as and when needed for installation.

i)  Other general terms and conditions as applicable for similar contracts for Civil, Mechanical and Electrical  work at BHEL, Hyderabad

j)  All materials required for civil works & structural/fabrication works  (Cement, steel,  paints & structural steels etc.)  included in the vendors scope. However cement and steel will be issued by BHEL on cost recovery basis.

k)  BHEL will provide Electric power & Water at free of cost. The agency should make necessary arrangement for tapping from the approved source.
5.0
PROPOSED SCHEME OF TREATMENT BLOCK 03 

The acidic/chromium bearing effluents from the pickling section of Block – 03 shall be collected in an existing holding tank and then will be pumped to the reaction tank cum settling tank with agitator. The pH is adjusted by addition of sulphuric acid and required quantity of sodium bisulphate will be added. The effluent will then be agitated to ensure proper mixing of chemicals and reduction of  hexavalent chromium to its trivalent form. About 1 hour of reaction time will be provided following conversions of Cr 6+ to Cr 3+. Sodium hydroxide will be added to raise the pH to enable precipitation of the metal as their hydroxides. Suitable quantity of polyelectrolyte solution will be dosed and reaction time of 60 minutes will be  allowed following which the effluent will be allowed to settle under quiescent conditions. The solids will settle at the bottom and will be collected in the hopper and will be periodically withdrawn. The bottom sludge will be applied to the sludge drying beds for dewatering and drying. Underflow from the sludge drying beds will be led back to the holding/collection tank. The clear/ treated water will be discharged into the drain after pH correction. The proposed scheme of treatment is depicted in the Figure-3. Though not shown in the layout scheme, Plant bye pass shall be ensured in the event of maintenance
6.0     SIZES AND SPECIFICATIONS OF VARIOUS UNITS (CIVIL, ELECTRICAL AND MECHANICAL WORKS) FOR THE PROPOSED PLANT.

6.1 Civil Works:

The effluent shall be collected in existing underground tank of size 2.74 m X 1.74 m X 2.28 m. The tank shall be renovated and lined with acid proof tile and then the whole surface coated with epoxy paint.

Specification Table  No. 6.1.1
	UNIT
	CHROMIUM REDUCTION TANK + SETTLING TANK 

	Duty
	To reduce hexavalent chromium to its trivalent form and precipitate metal hydroxides and allow solid – liquid separation

	Number of Units
	One

	Size
	2.5 m X 2.0 m X 2.0 m SWD + 0.5 m FB ; Depth of hopper – 1.0 m.

	MOC
	RCC M-25 epoxy coated


Specification Table  No. 6.1.2
	UNIT
	SLUDGE DRYING BEDS

	Duty
	For dewatering and drying of sludge.

	Number of Units
	Two (to be used in a cyclic manner)

	Size
	2.0 m X 2.0 m X 0.1 m each

	MOC
	Base in PCC and walls in brick work.


6.2 Mechanical works:

Specification Table No. : 6.2.1

	UNIT
	PUMPS

	Duty


	 To pump wastewater for onward treatment. 

	No. of units 


	 Two ( one as 100% stand-by )

	Capacity


	4-6 cum/hr. 

	Head


	 10 m.

	Type


	 Helical rotor pump with hyplon rubber starter and SS rotor. 


Specification Table No. : 6.2.2

	UNIT
	AGITATOR

	Duty

	To mix chemicals and effluent/wastewater for treatment in reaction cum settling tank.

	No. of units 

	 One  

	Rating                           
	 2.0 HP

	Type 
	Slow speed paddle type

	MOC
	Shaft & paddle in SS 316

	Drive


	Electric motor coupled to speed reduction gear box.


Specification Table No. : 6.2.3

	UNIT
	SULPHURIC ACID TANK

	Duty

	To hold sulphuric acid

	No. of units 

	 One  

	Volume                             
	 500 liters

	MOC


	 HDPE


Specification Table No. : 6.2.4

	UNIT
	SODIUM BISULPHATE TANK 

	Duty

	To hold sodium bisulphate

	No. of units 

	 One  

	Volume                             
	 250 liters

	MOC


	 HDPE


Specification Table No. : 6.2.5

	UNIT
	POLYELECTROLYTE TANK 

	Duty

	To hold Polyelectrolyte

	No. of units 

	 One  

	Volume                             
	 50 liters

	MOC


	 HDPE


Specification Table No. : 6.2.6

	UNIT
	SODIUM HYDROXIDE TANK 

	Duty

	To hold sodium hydroxide

	No. of units 

	 One  

	Volume                             
	500 liters

	MOC


	 HDPE


Specification Table No. : 6.2.7

	UNIT
	AGITATOR

	Duty

	To enable preparation of chemical solutions

	No. of units 

	 Three  

	Rating                           
	 1.0 HP

	Type 
	Slow speed paddle type

	MOC
	Shaft & paddle in SS 316

	Drive


	Electric motor coupled to speed reduction gear box.


Specification Table No. 6.2.8

	UNIT
	SULPHURIC ACID DOSING PUMP

	Duty
	To dose sulphuric acid in a regulated manner

	Number of Units
	Two (1 working +1 standby)

	Capacity                    
	0-6 lph each @ 5 m head  

	Type            
	Electronic variable dosing

	Make
	e- dose, Etatron or equivalent


Specification Table No. 6.2.9

	UNIT
	SODIUM BISULPHATE DOSING PUMP

	Duty
	To dose sodium bisulphate in a regulated manner

	Number of Units
	Two (1 working +1 standby)

	Capacity                    
	0-6 lph each @ 5 m head  

	Type            
	Electronic variable dosing

	Make
	e- dose, Etatron or equivalent


Specification Table No. 6.2.10

	UNIT
	POLYELECTROLYTE DOSING PUMP

	Duty
	To dose polyelectrolyte in a regulated manner

	Number of Units
	Two (1 working +1 standby)

	Capacity                    
	0-6 lph each @ 5 m head  

	Type            
	Electronic variable dosing

	Make
	e- dose, Etatron or equivalent


Specification Table No. 6.2.11

	UNIT
	SODIUM HYDROXIDE DOSING PUMP

	Duty
	To dose sodium hydroxide in a regulated manner

	Number of Units
	Two (1 working +1 standby)

	Capacity                    
	0-6 lph each @ 5 m head  

	Type            
	Electronic variable dosing

	Make
	e- dose, Etatron or equivalent


Specification Table No. 6.2.12

	UNIT
	RATE OR FLOW METER

	Duty


	 To measure the rate of flow  

	No. of units 


	 One

	Type


	 Suitable flow meter (Electro Magnetic) to measure instantaneous and cumulative flow with digital display. (0-700 KLD). Make Forbes marshall/Endress & Hauser. 


Specification Table No. : 6.2.13

	UNIT
	MOTOR CONTROL CENTER

	Duty
	For operation and protection of all electrical items starters.

	Incoming
	MCCB of adequate rating, ammeter, voltmeter, copper bus bar and phase indicating lamps.

	Out going
	Contactors of suitable rating of DOL type for motor rating up to 10 HP and Star-Delta type for motor ratings above 10 HP, thermal overload relay with built-in single phase preventer and HRC fuses for extra protection.

	Make
	All electrical items shall be of L&T, English Electric, GEC, Crompton, IMP,MECO or Siemens.

Separate panels shall be provided for each of the streams being fed to the ETP

	Electrical cabling 


	All interconnecting cabling within ETP shall be in PVC insulated, armored /unarmored, aluminum conductor of standard make. Cabling, as far as practicable, shall be underground.


Specification Table No. : 6.2.14

	UNIT
	INTERCONNECTING PIPING AND VALVES

	Duty
	Interconnection     between    the various units of the STP.

	Type


	a)  Piping : Generally all  piping shall  be in HDPE/PVC/GI/CI and of suitable size & pressure rating. 

b)  All   valves   shall   be  of  polypropylene/CI/GM


 





Specification Table No. 6.2.15

	UNIT
	ERECTION & COMMISSIONING

	Duty
	To erect the effluent treatment plant. After erection of the effluent treatment plant, the entire plant shall be commissioned to obtain the desired results. An operation and maintenance manual (3 copies) shall also be provided to the client. Necessary approval / clearance shall be obtained from the statutory authorities.


Specification Table No. 6.2.16

	UNIT
	Operation & maintenance

	Duty
	The effluent treatment plant has to be operated and maintained for a period of 24 months after obtaining the desired results / approval from the statutory authorities. All consumables, treatment chemicals, labour, repair and maintenance for regular running of the effluent treatment plant shall have to be borne by the tenderer. Periodical monitoring of treated effluents from PCB approved laboratory and packing & stacking of dried sludge in the ETP vicinity is in the scope of contractor.


Specification Table No. 6.2.17

	UNIT
	INTERCONNECTING PIPING AND VALVES


	SI.

No.
	From
	To
	Size
	Material

	
	
	
	Mm
	

	1
	Existing collection/holding  Tank
	Chromium reduction tank cum settling tank
	150 dia
	HDPE

	2
	Chromium reduction tank cum settling tank
	Sludge Drying bed
	150 OD
	HDPE

	3
	Chromium reduction tank cum settling tank
	Main drain
	150 OD
	HDPE

	4
	Sludge drying beds

Filtrate
	Existing collection/holding  Tank
	100 OD
	HDPE

	5
	Sulphuric Acid Tank 
	Chromium Reduction Tank
	100 Dia
	    HDPE

	6
	Sodium Sulphite Tank
	Chromium Reduction Tank
	100 Dia
	HDPE

	7
	Sodium Hydroxide Tank
	Chromium Reduction Tank
	100 Dia
	HDPE

	9
	Poly-electrolyte Tank
	Neutralisation Tank
	100 Dia
	HDPE


Note:

1)   Sluice valves should be of HDPE.

2)   The above quantity and size specified are indicative only. Tenderer shall access and quote   

       for the correct quantity and size indicating the requirement as per layout plan given.

4) Necessary Pipe & Valve as indicated in the plan to be provided for by-passing each unit 

                   in case of its cleaning in the scope of work
7.   SPECIFICATION OF ELECTRICAL WORKS : ( For Block - 03 Effluent  treatment plant)

7.1   Scope of Work :

A) 
Supply, installation and commissioning of electrical motors required for the process of      

    
  suitable capacity and approved make.

 B) 
Supply, installation and commissioning of Motor Control Center. 

C) 
Supply, installation and commissioning of any cabling required for remote  

control/interlocking purpose between vendors equipment and MCC, which includes  

control   cable if any.

H) Supply, laying, termination and commissioning of control cable of suitable size from  MCC 

to   push Button stations.

E) 
Supply, laying termination and commissioning of L T power cable of suitable sizes from      

             MCC to  all the motors and from MCC to main lighting distribution board.

I) Supply, installation and commissioning of required no, of push buttons stations to be 

located  near all the motors as per the chief Electrical Inspectorate Government of   Andhra Pradesh.

G)
 Lighting of control house at Effluent treatment plant only which consists of the following:

a) Supply, fixing and commissioning of  phases 4 ways 32 amp, MCB distribution of  

    approved make i.e.,. incomer 32 amp.

b)  5amp. Plug point - 2 Nos. and 15 A plug point - 2 nos. with sockets/switch boxes

c)  Suitable numbers of Fluorescent tube light fittings with dual tube lights shall be considered. 

Necessary cablings and poles for outside are also in the scope of the contractor.

Complete wiring with suitable wire for the above pump house works to be done by the contractor. i.e. from main distribution board to light point/power points, including switches and switch boards. Necessary power supply for the plant operation will be provided by BHEL-Hyderabad at plant room.

Earthing of all motors, MCC. Push buttons, main lightning DB and light points/power point etc. is included in scope.

The following guidelines shall be used for earthing.

For MCC  




 - GI flat 25x 6mm

For motors up to 10 HP & PB stations and main lighting DB 
  - GI 8 gauge

For motors above 10 HP





- 25x 3 mm GI flat

For main lighting DB to light points/power points 


- 2..5 sq. mm copper wire. 

Construction of masonry work chamber for two earth pits with GI covers.

Approval from the chief Electrical Inspector/Local EB authorities if required to be obtained by bidder. However, any statutory fees paid shall be reimbursed against submission of documentary (Proof including preparation and submission of drawing).

Sufficient length of rubber mats for MCC, Danger Board and 2 no. shock treatment charts. All externally mounted electric motor and reduction gears should be provided with weather shelf for protection from taint. 

Details to be furnished by contractor:

Exact ratings of all electrical loads in HP and KW and Total power requirement shall be indicated. The number of the feeders with rating to be furnished so that power supply arrangement could be made.

The contractor shall submit the following to the client for approval during engineering of contract.

i) A Schedule giving details of all motors.

ii) Single line diagram of MCC giving details of ratings of equipment like bus bar, Switch fuses, contractors, thermal relays etc., cable sizes etc., MCC drawing also to be submitted for approval.

 iii) A wiring Diagram showing: Terminal Nos. for connection for interconnecting cables at items of equipment's.

Schematic diagram showing inter looking sequence and control schemes, complete lighting layout showing the single line diagram.

7.2   Exclusions:

The main incoming power cable to MCC for the Effluent plant shall be in the purchaser's scope .

7.3   MCC Panel:

MCC panel shall provide power supply to various connected electrical installations and shall also include control circuits for operation of the equipment's as detailed under:

The MCC shall be compartmentalized self standing with bottom cable entry and cable alley arrangements. The panel shall be fabricated from CRCS sheets of not less than 16 SWG. The angle frame structure shall be provided for sturdiness.

The MCC shall have two incomers interlocked MCCBs ( 4 poles) , out going feeders, controlled circuits etc. The rating of various components of the MCC shall be based on the connected load to be provided by the supplier.

The MCC shall have base frame fabricated from 75x40 M.S. channels. The compartment door should have interlock with switch in such a way that it can open only when the switch is in off position. The door should have flexible connections to the frame for earthing. The panel shall have earth bus running for full length of the panel. The panel shall be earthed at 2 places. The panel shall be epoxy painted with zinc rich epoxy primer of not less than 100 micron. The panel shall include level controllers. However the level controllers excluding sensor can be mounted in a separate panel fabricated for CRCS sheet of SWG with wall mounting arrangement. The sensor should be float operated. The sheet and the counter shall be of SS 316 and shall move inside HOPE pipe. The level indicator shall be calibrated from the depth of the sump/tank. It shall be possible to stop the drive from push button stations located nearer each pump. The inscription of each feeder shall be as per approved drawing.

Each pump which are located outside the pump house shall be provided with rain hood.

Paint shade shall be shade 631 of IS:5. Enclosure protection class shall be IP54 for MCC panel and for PB station it shall be IP 55.

The incomers shall be provided with voltmeter with selector switch and ammeter with selector switch & 3 phase energy meter. The individual feeders shall be provided with switch fuse unit, contactors, thermal overload relays, on /off/ trip push buttons & indicating lamps.

7.4  CABLING:

The cabling shall be by means of armored cable of suitable sizes. The minimum size for the power cable shall be 4 sq. mm aluminum or 1.5 sq. mm copper and all control shall be based on continuous current rating and also voltage drop shall be limited to 2.5%. Their termination shall be by means of lugs of approximate size BI metallic lugs should be used where ever 2 different types of metal are involved at the junction. No intermediate cable joint shall be permitted unless route length exceeds 500 Mts.

Cable indicates connections between MCC panel, local start/stop push button stations / motors. Cables laid in trenches shall be provided with sand covering.

Only ISI approved make of cables shall be accepted with test certificates furnished. Cables crossing roads shall be provided with casing pipes with proper protection. The tentative outgoing feeders and ratings details are as given below.

	Recirculation Pump for CRT
	1HP
	I No. + I spare feeder

	Recirculation Pump for COT
	1HP
	I No. + I spare feeder

	NaOH Dosing Pump
	0.5 HP
	I no + I spare feeder.

	Effluent Transfer pump
	2 HP
	2 nos.


Note: These are indicative only. Actual rating are to be finalised by the tenderer based on the final design
Plus 2 Nos. TPN switch fuse for auxiliary duties(1 No.63 amp, S.F and I No. 32 amp. S.F. for welding and lighting.).

The tenderer to provide the actual out going feeder details.& single line diagram indicating pump rating and feeder ratings.

General notes:

5. All internal surfaces shall be provided with 20mm thick smooth cement plaster with water proofing compound in CM 1:4 unless otherwise specified. All exposed surfaces above ground level shall be plastered with 20 mm thick sand plaster in 2 coats of 12 mm and 8 mm thick and all external surfaces will be painted with cement paint of approved make and shade. The flooring of the tanks shall be 40mm thick IPS flooring in PCC 1 :2:4 with necessary slope etc., complete. All the structure shall be water tight. All ground level and above ground level structures tanks shall be provided with hand rails and ladders as necessary to suit site conditions with MS pipes.

6. The existing holding tank of size 2.74 m x 1.74 m x 2.28m will be renovated and lined with acid proof tile and then the whole surface coated with epoxy paint.

7. All external surface would be suitably painted with cement paint of good quality. Colour will be finalized in consultation with BHEL, Hyderabad

8. Name plate to be displayed on each unit and an overall layout be separately displayed

8.   DOCUMENTATION

	Document details
	Time schedule

	 Flow diagram of Block 03 ETP, layout of ETP OGA, SLD, BOM, scheme of electrical panels, PB station. OGA of mechanical equipments data sheet of various mechanical .item and cable, pipes. Pump and fan characteristics data sheet. etc.,
	 With in 4 weeks after LOL

	Piping schedule. Cable schedule, routing, Lighting layout. Earthing  schedule etc.,
	With in 6 weeks after LOI,

	Test certificates of all electrical items, mechanical items, material test certificates.
	Atleast one week prior to inspection of he equipments at vendor's premise.

	O&M manual with catalogues, recommended list of spares.
	Along with equipment dispatch.

	As built drawings ( 1 RTF + 7 sets)
	Before handing over equipment

	Chemical dosage for chromium and cyanide treatment
	Before handing over ETP

	Testing kit for analysis of Cyanide and Chromium
	Before handing over ETP


 8.1  The following documentation shall be submitted during execution as per schedule given :

8.2
The number of sets to be furnished shall be six. Manufacturing clearance shall be given to supplier for individual equipment after the corresponding drawing is approved by BHEL .

8.3
Bill of material shall indicate the make of supplier. Phrases like "equivalent! reputed" etc is not accepted. Correct make of the equipment shall be mentioned.

8.4
The drawing size shall be A3/A4/A2 and all other sizes will not be acceptable. The equipment dispatch  details and packing list shall be clearer so that all sub parts are identifiable by a label given by supplier.

8.5
All equipment drawings are to be submitted in 7 sets for approval and after they are approved manufacturing clearance shall be given for individual items. The supplier shall give inspection call along with internal test certificates 10 days prior to inspection & testing. The equipments are to be inspected by our Engineers before dispatch and only after getting clear dispatch instructions and equipment should be dispatched. 

8.6
The O&M manual shall broadly cover (a) Brief process, description and flow sheet, (b) 

Design parameters of flow and treated effluent characteristics. (c) Unit wise function and Number of description of plant start up procedure. (d) Equipment wise details operational instruction, maintenance procedure and (e) Analysis methods for relative parameters (based on standard method)

Figure-3

[image: image3.jpg]FlauRE-3

Exsting
<olLLECTION]

HOLDIND TANK|

Ha S04 ‘l

SopIUM No. oW soly

BisULPHITE

PoLy
ELECTROLYRE

*)DosinG
bbap

CHROMI M
REDUCTION TANK
M SE

DosING
(D besinG puMp iy

PoSING
Pump

» TREATED EFFLOENT 10
MAIK DRAN.

SLUDGE DRYING
BED

BLOCK-03

UNDER FLow FRoM SLUDAE
DRYING BED To COLLECTION,
HOLDING TANK





ANNEXURE - I       TOLERANCE LIMITS FOR Discharge from ETP

General Standards for Discharge of Environment Pollutants

(Ref: Schedule – VI Environmental (Protection) Rules’1986)

(All parameters except pH are in mg/L)

	S.No.
	Parameter
	Inland Surface Water

	1.
	Oil & Grease
	10

	2.
	Suspended Solids
	100

	3.
	pH                       
	5.5 - 9.0

	4.
	BOD
	30

	5.
	COD
	250

	6.
	Sulphide                 
	2.0

	7.
	Dissolved Phosphate
	5.0

	8.
	Nitrate                  
	10

	9.
	Fluoride                 
	2.0

	10.
	Manganese
	2

	11.
	Vanadium
	0.2

	12.
	Iron                     
	3

	13.
	Phenols                  
	1.0

	14.
	Cyanide                  
	0.2

	15.
	Arsenic                  
	0.2

	16.
	Cadmium                  
	2.0

	17.
	Hexavalent Chromium      
	0.1

	18.
	Total Chromium
	2.0

	19.
	Copper                   
	3.0

	20.
	Mercury
	0.01

	21.
	Lead                     
	0.1

	22.
	Zinc                     
	5.0

	23.
	Nickel
	3.0

	24.
	Selenium
	0.05

	25.
	Total Residual Chlorine
	1.0

	26.
	Ammonical Nitrogen
	50

	27.
	Total Kjeldahl Nitrogen
	100

	28.
	Free Ammonia
	50


ANNEXURE 2 : LIST OF RELEVANT CODES AND STANDARDS:

	Sl.no
	Indian standards No.
	Description

	1
	IS: 456-1978 REV 3
	Code of Practice for plain and reinforced

	
	AMEMD2
	concrete (second division)

	2
	IS : 3370
	Code of Practice for concrete structures of

	
	
	the storage of liquids.

	
	Part I - 1965
	General requirements

	
	Part II - 1965
	Reinforced Concrete

	
	Part 111- 1967
	Pre stressed concrete structures.

	
	Part IV- 1967
	Design Tables

	3.
	IS: 1536-1989
	Centrifugal cast(spun) iron pressure pipes

	
	
	for water, gas & sewage.

	4
	IS: 1537 -1976
	Vertically cast iron pressure pipes for water,

	
	
	gas and sewage.

	5
	IS: 1538-1993
	Cast Iron fittings for pressure pipes for

	
	
	water, gas and sewage.

	6
	IS : 3114 - 1994
	Code for practice for laying of CI pipes.

	7.
	IS : 782-1978
	Caulking Lead.

	8.
	IS : 7634 - 1975 part II
	code of practice for laying and jointing of high density

	
	
	polyethylene pipes.

	9
	IS : 5639 - 1970
	Pumps handling chemicals & corrosive

	
	
	liquids.

	10
	IS: 2685 -1971
	Code of practice for selection, installation and

	
	
	maintenance of sluice valves.



BHARAT HEAVY ELECTRICALS LIMITED

HYDERABAD

TECHNICAL SPECIFICATIONS OF

 EFFLUENT TREATMENT PLANT- MOTOR TRANSPORT AREA
INDEX
	SL.NO
	DESCRIPTION
	
	PAGE NO.

	1
	INTRODUCTION
	2

	2
	PRESENT STATUS
	3

	3
	BASIC DATA
	3

	4
	SCOPE OF WORK 
	5

	5
	PROPOSED SCHEME OF CONTRACT
	6

	6
	SIZES AND SPECIFICATIONS OF VARIOUS UNITS (CIVIL, ELECTRICAL &MECHANICAL WORKS)
	7

	7
	SPECIFICATION OF ELECTRICAL WORKS
	14

	8
	DOCUMENTATION
	
	18

	ANNEXURE
	
	
	

	1
	 ETP SCHEMATIC LAYOUT (FIGURE-1)
	20

	2
	TOLERANCE LIMITS FOR DISCHARGE FROM ETP (ANNEXURE-1)
	21

	3
	 LIST OF RELEVANT CODES & STANDARDS (ANNEXURE-2)
	22


Deviations from the specifications if any, shall be clearly brought out by the bidder with sufficient explanation separately at the end, giving reference to the clause number in the specification. Otherwise it will be presumed that the tender in total conformity is accepted by the bidder
EFFLUENT TREATMENT PLANT- MOTOR TRANSPORT AREA

1. 
INTRODUCTION.

The BHEL Hyderabad unit was set up in 1963 and started its operations with manufacture of Turbo-generator sets and auxiliaries for 60 and 110 MW thermal utility sets. Over the years it has increased its capacity range and diversified its operations to many other areas. 

The factory is situated at Ramchandrapuram, approximately 23Km.  from Secundrabad Railway Station. At present there are about 6000 employees working in the plant. The township is situated adjacent to the factory having population of approximately 30,000 with about 4600 staff quarters. 

The manufacturing facilities at BHEL, Hyderabad include:

xxxi. TC&GT  -Block-01

xxxii. Electrical Machines – Block-02

xxxiii. Switch Gear and Breaker  Block-03

xxxiv. Foundry & Pattern making shop – Blocks - 04,05&09

xxxv. Heat Exchanger/Fabrication-Block-06

xxxvi. Tool Room Block-07

xxxvii. Heat Treatment and common work shop –Block-08

xxxviii. Pump manufacturing block –70

xxxix. Bowl Mill & Oil field Equipment – Block-51

xl. Services Department

· Transport

· Compressor House

· Producer Gas Plant

· Boiler House

· Diesel Power House

· Canteens

· Oxygen plant

The motor transport unit handles the maintenance of the various vehicles in the Plant. One of the major operations undertaken here is the washing of the vehicles. Around 8 to 10 vehicles are washed here daily. The water consumed for washing one vehicle is estimated to be around 500 liters. Thus 5 KL of effluent is generated from this unit. 

6. PRESENT STATUS

During washing of the various vehicles in the Motor Transport Area, effluent to the tune of 5 KLD is generated. The effluent is taken to an underground tank where the oil deposit on the surface is skimmed off and the effluent discharged into the industrial drain. The ingress of oil and grease in the main drain leads to a load on the main Sewage treatment plant.

Hence the need was felt to have a separate Effluent treatment plant for treating the effluents from Motor transport.  The following treatment is envisaged:

1. A proper ETP with Oil and Grease trap needs to be built at Motor transport area to effectively remove grit and Oil & Grease.

2. The effluent after oil & grease removal needs to be treated with alum to remove any suspended solids and traces of oil.

3. The water after treatment is discharged into the main drain.

1.0 BASIC DATA: 

The basic data considered for preparing schematics and sizing of unit operations of effluent treatment plant are given below::

a)  Wastewater quantity: 5 m3 / day 

 b) Characteristics of raw wastewater: The characteristics of the effluent considered for designing the treatment for motor transport area are as given in table below:

TABLE: CHARACTERISTICS OF RAW WASTEWATER

	Sr. No.
	Parameter
	Concentration

	1
	COD
	200 - 250

	2
	Oil & Grease
	15 – 25

	3
	TSS
	200 - 250


*All parameters expressed in mg/l

c) Characteristics of treated wastewater: The expected characteristics of the treated wastewater on adopting the scheme of treatment given in  S.N. 5 are given in table below:
TABLE: CHARACTERISTICS OF TREATED WASTEWATER 

	Sr. No.
	Parameter
	Concentration



	1
	COD
	< 250

	2
	Oil & Grease
	< 10

	3
	TSS
	< 50


 *All parameters expressed as mg/l

4.
SCOPE OF CONTRACT

Scope of work shall broadly include design, construction, erection & commissioning of effluent treatment plant  for Motor Transport Area & operating the plant for a period of 2 years  as per conceptual design and specifications given in Figure - 4. The tenderer should give the treated effluent quality confirming with the Andhra Pradesh State Pollution Board Standards (consent condition), as well as the parameters specified in Schedule VI of Environmental Protection rules 1986 (annexure-1).

The following items are included with in the scope of work :

a)
All the civil works and structural fabrication works of the treatment plant as per the detailed description of the civil works and generally as per the layout. Detailed drawings with tentative levels of individual structure are also to be prepared. The contactor shall get the detailed civil and Engineering drawing approved by BHEL prior to initiation of civil work at site.  Schematic of the ETP is enclosed herewith.

b)
Supply, erection and commissioning of all the equipment's required for the treatment plants as per the individual equipment's specifications and details given herewith.

c)
The scope of work includes all necessary civil works, like construction MCC / control room, panel foundation, cable trenches cable supports, pipe supports, lighting of pump house etc. complete. The scope of work also includes in providing the puddle insert drawings as required for each unit operation of the Treatment Plant as per the envisaged scheme & layout plan.

d)
The scope of work also includes de-linking the of the existing drain, and connecting the drain to the proposed holding tank, this being the first level of the unit operation of the Effluent treatment plant in Motor Transport Area and re-linking the final treated discharge line to the Industrial drain. The agency has to inspect the site to ensure the invert level of the inlet pipe near the ETP site and also treated water receiving drain.

e)
Obtaining all necessary statutory approvals from Andhra Pradesh State Pollution Control Board and other statutory bodies for construction and commissioning are included in the scope of work of contractor.

f)
The Horse Power (HP) of all the pumps, blower etc. shown are indicative. The actual HP shall be furnished by the contractor to meet the specified flow and head.

g)   Documentation shall be furnished as per clause 8.0.

h)
All temporary sheds, offices, go downs etc., required for storage of materials and for contractors supervisory personnel at site is the scope of the bidder. The required equipments and materials are to received and stored by the bidder and to be issued as and when needed for installation.

i)
Other general terms and conditions as applicable for similar contracts for Civil, Mechanical and Electrical  work at BHEL, Hyderabad

j)  All materials required for civil works & structural/fabrication works  (Cement, steel,  paints & structural steels etc.)  included in the vendors scope. However cement and steel will be issued by BHEL on cost recovery basis.

k)  BHEL will provide Electric power & Water at free of cost. The agency should make necessary arrangement for tapping from the approved source.

5. PROPOSED SCHEME OF EFFLUENT TREATMENT

The effluent from the Motor Transport area will be collected in a sump and then will be discharged to the ETP. As the major pollutant in the effluent from this area is Oil & Grease and grit, it is proposed to collect the effluent in a holding tank and passed through screen and grit chambers,

The effluent would then be sent to a Oil & Grease trap for removal of Oil & Grease. After the removal of oil and grease, the effluent would then be passed over alum sump to coagulate the fine suspended particles before being clarified in settling tank. The overflow from settling tank is discharged into industrial drain.

The sludge generated in the ETP would be drained onto sludge drying bed.

The effluent would be retained in the holding tank for a period of 3 days and discharged twice a week.

The treated effluent which would meet the requirement of Schedule VI of Environment Protection Act and to be discharged into the main drain.

The proposed scheme of treatment plant for motor transport area would consist of the following units and as indicated in Figure- 4: Though not shown in the layout scheme, Plant bye pass shall be ensured in the event of maintenance.
The   proposed treatment  plant will consist of : 

10. Holding Tank

11. Screen Chamber

12. Grit Chamber

13. Oil & Grease trap

14. Alum sump

15. Settling tank

16. Sludge drying bed

17. Flow Measuring device

6. 
SIZES AND SPECIFICATIONS OF VARIOUS UNITS (CIVIL, ELECTRICAL AND  MECHANICAL WORKS) FOR THE PROPOSED PLANT.

6.1 Civil Works:

Specification Table  No. 6.1.1

	UNIT
	HOLDING TANK

	Duty
	To collect the effluent 

	Number of Units
	One

	Size
	2.3 m X 2.3 m X 1.0 m SWD

	MOC
	RCC M-20


Specification Table  No. 6.1.2
	UNIT
	SCREEN CHAMBER

	Duty
	For removal of coarse matter

	No. of units
	One

	Size
	1.0 m X 0.3 m X 0.3 m SWD

	MOC
	RCC M-20


Specification Table  No. 6.1.3
	UNIT
	GRIT CHAMBER 

	Duty
	To enable removal of sediments

	No. of units

	Two (to be used alternately) 

	Size
	2.3 m X 0.6 m X 0.5 m SWD

	MOC
	RCC M-20


Specification Table  No. 6.1.4
	UNIT
	OIL AND GREASE TRAP

	Duty
	To separate oil and grease.

	Number of Units
	Two

	Size
	2.5m x 2.5m x 1.5m SWD + 0.5 m FB

	MOC
	RCC M-20

	Provision
	Provision is to be made for housing of mechanical oil separators


Specification Table  No. 6.1.5
	UNIT
	ALUM SUMP

	Duty
	To increase floculation

	Number of Units
	one

	Size
	0.5m x0.5m x 1.0m SWD + 0.5 m FB

	MOC
	RCC M-20


Specification Table No.6.1.6

	UNIT
	SETTLING TANK

	Duty
	To enable solid liquid separation 

	No. of units
	One 

	Size          
	1.8 m X 1.8 m X 2.5 m SWD + 0.5 m FB

	MOC
	RCC M-20


Specification Table  No. 6.1.7
	UNIT
	SLUDGE DRYING BEDS

	Duty
	For dewatering and drying of sludge.

	Number of Units
	Two (to be used in a cyclic manner)

	Size
	3.0 m X 2.0 m X 1.0 m each

	MOC
	Base in PCC and walls in brick work.


6.2 Mechanical works:

Specification Table No. : 6.2.1

	UNIT
	PUMPS

	Duty


	 To pump wastewater for onward treatment. 

	No. of units 


	 Two ( one as 100% stand-by )

	Capacity


	2.0 cum/hr. 

	Head


	 10 m.

	Type


	 Non clog, self priming centrifugal pumps. 


Specification Table No. 6.2.2

	UNIT
	API TYPE OIL SEPARATOR

	Duty
	To separate oil and grease

	Number of Units
	One

	Capacity
	Comprising of 80mm Dia. MS pipe with perforations and tilting gear mechanism for skimming out the oil. The perforations on the pipe shall be 40mm x 80mm rectangular spaced at 120 mm c/c.

 No of Pipe required
-
 2 Nos.



	Make
	INDAVARA or equivalent




Specification Table No. : 6.2.3

	UNIT
	RATE OR FLOW METER

	Duty


	 To measure the rate of flow  

	No. of units 


	 One

	Type


	 Suitable flow meter (Electro Magnetic) to measure instantaneous and cumulative flow with digital display. (0-20 KLD). Make Forbes marshall/Endress & Hauser. 


Specification Table No. : 6.2.4

	      UNIT
	CONTROL UNIT

	Duty
	For operation and protection of all electrical starters.

	Incoming
	MCCB of adequate rating, ammeter, voltmeter, copper bus bar and phase indicating lamps.

	Out going
	Contactors of suitable rating of DOL type for motor rating up to 10 HP and Star-Delta type for motor ratings above 10 HP, thermal overload relay with built-in single phase preventer and HRC fuses for extra protection.

	Make
	All electrical items shall be of L&T, English Electric, GEC, Crompton, IMP, MECO or Siemens.

Separate panels shall be provided for each of the streams being fed to the RO

	Electrical cabling 


	All interconnecting cabling within ETP shall be in PVC insulated, armored /unarmored, aluminum conductor of standard make. Cabling, as far as practicable, shall be underground.


Specification Table No. : 6.2.5

	UNIT
	INTERCONNECTING PIPING AND VALVES

	Duty
	Interconnection     between    the various units of the STP.

	Type


	a)  Piping : Generally all  piping shall  be in HDPE/PVC/GI/CI and of suitable size & pressure rating. 

b)  All   valves   shall   be  of  polypropylene/CI/GM


Specification Table No. 6.2.6

	UNIT
	ERECTION & COMMISSIONING

	Duty
	To erect the WWTP. After erection of the WWTP, the entire plant shall be commissioned to obtain the desired results. An operation and maintenance manual (3 copies) shall also be provided to the client. Necessary approval / clearance shall be obtained from the statutory authorities.


Specification Table No. 6.2.7

	UNIT
	Operation & Maintenance

	Duty
	The WWTP has to be operated and maintained for a period of 24 months after obtaining the desired results / approval from the statutory authorities. All consumables, treatment chemicals, labour, repair and maintenance for regular running of the WWTP shall have to be borne by the tenderer. Periodical monitoring of treated effluents from PCB approved laboratory and packing & stacking of dried sludge in the ETP vicinity is in the scope of contractor.


Specification Table No. 6.2.8

	UNIT
	INTERCONNECTING PIPING AND VALVES


	SI.

No.
	From
	To
	Size
	Material

	
	
	
	mm
	

	1
	Holding tank
	Bar Screen
	150 OD
	CI insert-l no

	2
	Bar Screen
	Grit Chamber
	150 OD
	CI insert-l no

	3
	Grit Chamber
	Oil & Grease tank
	150 OD
	CI insert-l no

	4
	Oil & Grease tank 
	Alum Sump
	150 OD
	CI insert -2 No

	5
	Alum Sump
	Settling tank
	150 OD
	CI insert -2 No.



	6
	Settling tank 
	Sludge drying bed
	100 OD
	CI insert -2 No.



	7
	Settling tank
	Industrial drain
	150 OD
	CI insert -2 No

	8.
	Sludge Drying bed
	Holding tank
	150 OD
	CI insert -2 No


Note:

1)   Sluice valves should be of cast Iron only.

2)  The above quantity and size specified are indicative only. Tenderer shall access and quote for the correct quantity and size indicating the requirement as per layout plan given.

5) Necessary Pipe & Valve as indicated in the plan to be provided for by-passing each unit in case of its cleaning in the scope of work.

7.   SPECIFICATION OF ELECTRICAL WORKS : (For Effluent  treatment plant for    Motor Transport area)

7.1   Scope of Work :

A) 
  Supply, installation and commissioning of electrical motors required for the process of      

    
  suitable capacity and approved make.

 B) 
Supply, installation and commissioning of Motor Control Center. 

C) 
Supply, installation and commissioning of any cabling required for remote  

control/interlocking purpose between vendors equipment and MCC, which includes  

control   cable if any.

A) Supply, laying, termination and commissioning of control cable of suitable size from  MCC 

to   push Button stations.

E) 
Supply, laying termination and commissioning of L T power cable of suitable sizes from      

             MCC to  all the motors and from MCC to main lighting distribution board.

B) Supply, installation and commissioning of required no, of push buttons stations to be 

located  near all the motors as per the chief Electrical Inspectorate Government of   Andhra Pradesh.

G)
 Lighting of pump house at Effluent treatment plant only which consists of the following:

a) Supply, fixing and commissioning of3 phases 4 ways 32 amp, MCB distribution of  

    approved make i.e.,. incomer 32 amp.

b)  5amp. Plug point - 2 Nos. and 15 A plug point - 2 nos. with sockets/switch boxes

c)  Sufficient  nos. of Fluorescent tube light fittings with dual tube lights shall be considered. 

Necessary cablings and poles for outside are also in the scope of the contractor.

Complete wiring with suitable wire for the above pump house works to be done by the contractor. i.e. from main distribution board to light point/power points, including switches and switch boards. Necessary power supply for the plant operation will be provided by BHEL-Hyderabad at plant room.

Earthing of all motors, MCC. Push buttons, main lightning DB and light points/power point etc. is included in scope.

The following guidelines shall be used for earthing.

For MCC  




 - GI flat 25x 6mm

For motors up to 10 HP & PB stations and main lighting DB 
  - GI 8 gauge

For motors above 10 HP





- 25x 3 mm GI flat

For main lighting DB to light points/power points 


- 2..5 sq. mm copper wire. 

Construction of masonry work chamber for two earth pits with GI covers.

Approval from the chief Electrical Inspector/Local EB authorities if required to be obtained by bidder. However, any statutory fees paid shall be reimbursed against submission of documentary (Proof including preparation and submission of drawing).

Sufficient length of rubber mats for MCC, Danger Board and 2 no. shock treatment charts. All externally mounted electric motor and reduction gears should be provided with weather shelf for protection from taint. 

Details to be furnished by contractor:

Exact ratings of all electrical loads in HP and KW and Total power requirement shall be indicated. The number of the feeders with rating to be furnished so that power supply arrangement could be made.

The contractor shall submit the following to the client for approval during engineering of contract.

i)
 A Schedule giving details of all motors.

ii)
 Single line diagram of MCC giving details of ratings of equipment like bus bar, Switch fuses, contractors, thermal relays etc., cable sizes etc., MCC drawing also to be submitted for approval.

 iii)
 A wiring Diagram showing: Terminal Nos. for connection for interconnecting cables at items of equipment's.

Schematic diagram showing inter looking sequence and control schemes, complete lighting layout showing the single line diagram.

7.2   Exclusions:

The main incoming power cable to MCC for the Waste water treatment plant shall be in the purchaser's scope .

7.3   MCC Panel:

MCC panel shall provide power supply to various connected electrical installations and shall also include control circuits for operation of the equipment's as detailed under:

The MCC shall be compartmentalized self standing with bottom cable entry and cable alley arrangements. The panel shall be fabricated from CRCS sheets of not less than 16 SWG. The angle frame structure shall be provided for sturdiness.

The MCC shall have two incomers interlocked MCCBs ( 4 poles) , out going feeders, controlled circuits etc. The rating of various components of the MCC shall be based on the connected load to be provided by the supplier.

The MCC shall have base frame fabricated from 75x40 M.S. channels. The compartment door should have interlock with switch in such a way that it can open only when the switch is in off position. The door should have flexible connections to the frame for earthing. The panel shall have earth bus running for full length of the panel. The panel shall be earthed at 2 places. The panel shall be epoxy painted with zinc rich epoxy primer of not less than 100 micron. The panel shall include level controllers. However the level controllers excluding sensor can be mounted in a separate panel fabricated for CRCS sheet of SWG with wall mounting arrangement. The sensor should be float operated. The sheet and the counter shall be of SS 316 and shall move inside HOPE pipe. The level indicator shall be calibrated from the depth of the sump/tank. It shall be possible to stop the drive from push button stations located nearer each pump. The inscription of each feeder shall be as per approved drawing.

Each pump which are located outside the pump house shall be provided with rain hood.

Paint shade shall be shade 631 of IS:5. Enclosure protection class shall be IP54 for MCC panel and for PB station it shall be IP 55.

The incomers shall be provided with voltmeter with selector switch and ammeter with selector switch & 3 phase energy meter. The individual feeders shall be provided with switch fuse unit, contactors, thermal overload relays, on /off/ trip push buttons & indicating lamps.

7.4  CABLING:

The cabling shall be by means of armored cable of suitable sizes. The minimum size for the power cable shall be 4 sq. mm aluminum or 1.5 sq. mm copper and all control shall be based on continuous current rating and also voltage drop shall be limited to 2.5%. Their termination shall be by means of lugs of approximate size BI metallic lugs should be used where ever 2 different types of metal are involved at the junction. No intermediate cable joint shall be permitted unless route length exceeds 500 Mts.

Cable indicates connections between MCC panel, local start/stop push button stations / motors. Cables laid in trenches shall be provided with sand covering.

Only ISI approved make of cables shall be accepted with test certificates furnished. Cables crossing roads shall be provided with casing pipes with proper protection. Plus 2 Nos. TPN switch fuse for auxiliary duties(1 No.63 amp, S.F and I No. 32 amp. S.F. for welding and lighting.).

The tenderer to provide the actual out going feeder details.& single line diagram indicating pump rating and feeder ratings.

General notes:

9. All internal surfaces shall be provided with 20mm thick smooth cement plaster with water proofing compound in CM 1:4 except pump house structure unless otherwise specified. All exposed surfaces above ground level shall be plastered with 20 mm thick sand plaster in 2 coats of 12 mm and 8 mm thick and all external surfaces will be painted with cement paint of approved make and shade. The flooring of the tanks shall be 40mm thick IPS flooring in PCC 1 :2:4 with necessary slope etc., complete. All the structure shall be water tight. All ground level and above ground level structures tanks shall be provided with hand rails and ladders as necessary to suit site conditions with MS pipes.

10. Calibration chart indicating depth of Flow with Effluent Quantity to be provided.

11. All Surface would be suitably painted with cement paint of good quality. Colour will be finalized in consultation with BHEL, Hyderabad

12. Name plate to be displayed on each unit and an overall layout be separately displayed

8.   DOCUMENTATION

	Document details
	Time schedule

	 Flow diagram of ETP, layout of ETP OGA, SLD, BOM, scheme of electrical panels, PB station. OGA of mechanical equipments data sheet of various mechanical .item and cable, pipes. Pump and fan characteristics data sheet. etc.,
	 With in 4 weeks after LOL

	Piping schedule. Cable schedule, routing, Lighting layout. Earthing  schedule etc.,
	With in 6 weeks after LOI,

	Test certificates of all electrical items, mechanical items, material test certificates.
	Atleast one week prior to inspection of he equipments at vendor's premise.

	O&M manual with catalogues, recommended list of spares.
	Along with equipment dispatch.

	As built drawings ( 1 RTF + 7 sets)
	Before handing over equipment


8.1
The following documentation shall be submitted during execution as per schedule given below:

8.2   The number of sets to be furnished shall be six. Manufacturing clearance shall be given to supplier for individual equipment after the corresponding drawing is approved by BHEL .

8.3  
Bill of material shall indicate the make of supplier. Phrases like "equivalent! reputed" etc is not accepted. Correct make of the equipment shall be mentioned.

8.4 
The drawing size shall be A3/A4/A2 and all other sizes will not be acceptable. The equipment dispatch  details and packing list shall be clearer so that all sub parts are identifiable by a label given by supplier.

8.5
 All equipment drawings are to be submitted in 7 sets for approval and after they are approved manufacturing clearance shall be given for individual items. The supplier shall give inspection call along with internal test certificates 10 days prior to inspection & testing. The equipments are to be inspected by our Engineers before dispatch and only after getting clear dispatch instructions and equipment should be dispatched. 

The O&M manual shall broadly cover (a) Brief process, description and flow sheet, (b) Design parameters of flow and treated effluent characteristics. (c) Unit wise function and Number of description of plant start up procedure. (d) Equipment wise details operational instruction, maintenance procedure and (e) Analysis methods for relative parameters (based on standard method).

Figure-4

[image: image4.jpg][Faure |

RAW EFFLUENT
FROM MT AREA

o

sUME

/ ARITCHAMBSER

O B EREASE]

HOLDING TANK

SEREEN CHAMBER

-t

SLUDGE DRYING

MOTOR TRANSFORT AREA

PiscuaRa &
\

ALum.
SUMP

SET ThiNg
TAnk

BEDS

UNDER FLOwW OF SLUDGE
DRYWG BEDTHHOLDING TANK

—

[
—






ANNEXURE - I       TOLERANCE LIMITS FOR ETP 

General Standards for Discharge of Environment Pollutants

(Ref: Schedule – VI Environmental (Protection) Rules’1986)

(All parameters except pH are in mg/L)

	S.No.
	Parameter
	Inland Surface Water

	1.
	Oil & Grease
	10

	2.
	Suspended Solids
	100

	3.
	pH                       
	5.5 - 9.0

	4.
	BOD
	30

	5.
	COD
	250

	6.
	Sulphide                 
	2.0

	7.
	Dissolved Phosphate
	5.0

	8.
	Nitrate                  
	10

	9.
	Fluoride                 
	2.0

	10.
	Manganese
	2

	11.
	Vanadium
	0.2

	12.
	Iron                     
	3

	13.
	Phenols                  
	1.0

	14.
	Cyanide                  
	0.2

	15.
	Arsenic                  
	0.2

	16.
	Cadmium                  
	2.0

	17.
	Hexavalent Chromium      
	0.1

	18.
	Total Chromium
	2.0

	19.
	Copper                   
	3.0

	20.
	Mercury
	0.01

	21.
	Lead                     
	0.1

	22.
	Zinc                     
	5.0

	23.
	Nickel
	3.0

	24.
	Selenium
	0.05

	25.
	Total Residual Chlorine
	1.0

	26.
	Ammonical Nitrogen
	50

	27.
	Total Kjeldahl Nitrogen
	100

	28.
	Free Ammonia
	50


ANNEXURE 2 : LIST OF RELEVANT CODES AND STANDARDS
	Sl.no
	Indian standards No.
	Description

	1
	IS: 456-1978 REV 3
	Code of Practice for plain and reinforced

	
	AMEMD2
	concrete (second division)

	2
	IS : 3370
	Code of Practice for concrete structures of

	
	
	the storage of liquids.

	
	Part I - 1965
	General requirements

	
	Part II - 1965
	Reinforced Concrete

	
	Part 111- 1967
	Pre stressed concrete structures.

	
	Part IV- 1967
	Design Tables

	3.
	IS: 1536-1989
	Centrifugal cast(spun) iron pressure pipes

	
	
	for water, gas & sewage.

	4
	IS: 1537 -1976
	Vertically cast iron pressure pipes for water,

	
	
	gas and sewage.

	5
	IS: 1538-1993
	Cast Iron fittings for pressure pipes for

	
	
	water, gas and sewage.

	6
	IS : 3114 - 1994
	Code for practice for laying of CI pipes.

	7.
	IS : 782-1978
	Caulking Lead.

	8.
	IS : 7634 - 1975 part II
	code of practice for laying and jointing of high density

	
	
	polyethylene pipes.

	9
	IS : 5639 - 1970
	Pumps handling chemicals & corrosive

	
	
	liquids.

	10
	IS: 2685 -1971
	Code of practice for selection, installation and

	
	
	maintenance of sluice valves.




















