ANNEXURE-1

SPECIFICATION FOR 500Hz SUPPLY SOURCE
Single Phase Motor Generator Set with Control Panel 
Rating: 120 KVA continuous.

Output Voltage: 0-1200 Volts

Current: 100 Amperes

Frequency: 500 Hz

Insulation: Class ‘H’

Motor Generator Set: It shall be drip proof and water proof up to shaft level with lifting hooks at appropriate locations. Earthing bolts shall be provided on the frame of each Motor Generator Set. Motor & Generator winding shall be suitably protected from surges, over/ under voltages, etc. Anti-condensation heaters shall be fitted in the MG set for both Motor and Stator.

Control Panel: It shall incorporate necessary controls and relays to operate and protect MG set. Digital calibrated meters (LCDs) are required to indicate input, output and fault conditions (voltage, current and frequency). It shall be suitable for minimum one hour continuous operation. 

Pre-inspection required at vendor works.

TC shall be furnished for winding resistance, insulation resistance, High Voltage withstand test, Open Circuit test, Short Circuit test and temperature rise test. 

OR SUITABLE ELECTRONIC STATIC PANEL FOR GENERATING UPTO 1000V, 200A, 500 Hz SOURCE
Party shall indicate other essential spares and optional accessories required for safe operation of the equipment for at least 5 years. 

· Party shall supply two copies of O & M Manual in English along with internal circuitry. 

· Equipment shall be commissioned free of cost at our premises. 

· T/C and G/C of the equipment are required.

· Calibration Certificate. 

· Party shall impart training for operation/ maintenance of the equipment at their works free of cost. 

· Party shall quote separately for “Annual Maintenance Contract” for 3 years mentioning no. of visits per year.

· Party shall indicate the service facility and service centre in Northern India.

· Party shall indicate self calibrating facility of the equipment, if available (optional).

