PAGE  
                                              





TECHNO COMMERCIAL SPECIFICATIONS-
FOR WALK IN COOLERS 
SELF STANDING SIZE 2.1M x 3.6M x 2.2M – 2 Nos  

Indent CG7P0218 dt 13/11/07


	S.N
	Description
	Requirement.
	Deviations
	Remarks

	1. 
	Prequalification of Vendor. 
	1.Annual FinancialTurnover during the last 3 years ending 31st March-2007 should be at least Rs.4.0 Lakhs

2.Experience of having successfully completed similar works  (chest freezers /  ice cream conservators/display cases /cold rooms/cold store equipments of nomilar capacity18000 BTU/hr) during last 7 years ending October-2007 should be either of the following.

2a. Three similar works costing not less than Rs.1.7 Lakhs each or 

2b.Two similar works costing not less than Rs.2.1 Lakhs each or

2c. One similar completed work costing not less than Rs.3.4 Lakhs 

Offer not satisfying the above requirements is  liable for rejection.
	
	

	2. 
	Walk-in-Cooler sizes
	For Works Canteen room size : 2.1m X 3.6 m X 2.22 m (Inside dims)-Self Standing walk-in-Cooler- Totally new-2 Nos.


	
	

	3. 
	Design temperature
	+ 40 C  ±  20 C
	
	

	4. 
	Floor Panels
	60 mm Modular Puff covered with marine Plywood with Antiskid Aluminum checkered sheet.
	
	

	5. 
	Skin material for panel
	 PCGI.-Blue Color
	
	

	6. 
	Door – Heavy duty, gasket, reliable and convenient locking system.
	0.9 M X 2.1 M Standard Size (Right hand side open)
	
	

	7. 
	Ambient Temp.
	 Max.500 C
	
	

	8. 
	Lighting
	Bulk head 2nos.
	
	

	9. 
	Product to be Stored.
	Vegetables & Milk
	
	

	10. 
	Pull down time
	10 to 12 hours
	
	

	11. 
	Refrigeration capacity required.
	18000 BTU / hour for 2 units together.

One unit working, other standby.
	
	

	12. 
	Configuration:
	The Refrigeration units are designed for 40 to 45 deg C condensing and -28 deg C evaporation temperature and suit to ambient temperature 40 to 50 deg. C.
	
	

	13. 
	Compressor make
	Kirloskar Copeland / Tecumseh or  equivalent
	
	

	14. 
	Compressor run time
	18 hours
	
	

	15. 
	Refrigerant
	R 22 
	
	

	16. 
	Power consumption
	Most economical. Party to specify.
	
	

	17. 
	Civil works.
	 Necessary civil works of removing existing conventional door, finishing the walls etc,. is in the scope and cost of the  party. To quote as lumpsum.

	
	

	18. 
	Mountings:
	Necessary platforms out side the room for installing refrigeration units shall be provided /erected by the party only.
	
	

	19. 
	Additional requirements:


	1. Hot air vent.

2. View Port.

3. Interior Safety Release system to prevent entrapment of people in the cold room.

4. Reliable and robust cam-locks, hinges etc,.

5. Vapour proof light fixtures in     the room.

6. Digital temperature indicator of  1” LED size shall be provided outside the room.

7. Watt-Hr Energy meter.
	
	

	20. 
	Above equipment Should be
	 Refrigeration unit and not Air Conditioning unit.
	
	

	21. 
	Configuration
	The standby  Refrigeration system required  is 100% standby. This is an independent unit with a separate condenser and Evaporator and can be switched  on in case of any breakdown of one machine.  


	
	


K.V.Krishna Nandan/M&S
PAGE  
4

