Tender No. M2/08/CG8P0250/UMR
Due Date. 17.04.2009
TECHNICAL SPECIFICATIONS FOR PU INSULATED PANELS – 30 MM
1). Supply of PU Panel System, consisting insulated sandwich panels, for  roofing & flashings, made out of CFC free Polyurethane Foam sandwiched between two metal sheets. 
Top sheet shall be made out of 0.5 MM  TCT, 550 Mpa 150 GSM Colour coated Galvalume sheets  with 20 microns of XRW/SMP coating of approved colour on the top over the 5 microns back up epoxy coating at the bottom over the 5 microns primer. 
These sheets will be in hi-rib profile with 34.5 mm crest height in 332.8 mm pitch with 999 mm covered width  and length upto a maximum of 12 M. Bottom sheet shall be plain ribbed 0.5 mm TCT, 550 Mpa 150 GSM colour Galvalume sheets  with 20 microns of XRW/SMP coating of approved colour on the top over the 5 microns back up epoxy coating at the bottom over the 5 microns primer. The polyurethane foam shall have 40 ± 2 Kg / Cu m density and 30 mm thickness.
2). Required lengths to be supplied by agency as per site requirement (not more than 12 meters length).

3). Insulated portion area only considered for measurement & payment (overlap portion will not be considered). 

