Enq.ref: PC:SD:81LCP:IOT:001/18.04.2014
Item: CONDENSATE PUMPS
Projects: :Lalitpur and Mouda projects

Due date : 23.05.2014, 1400 hrs
Kindly find the clarifications below in technical specification for the above mentioned enquiry.
i) Design fluid temperature of 135 Deg C shall be adopted. Head to be developed is given in run out condition. Bidder to arrive at the head that will be developed during rated condition.

ii) The Pumps are envisaged for being located in Boiler area. Kindly  consider  Motor design  suitable for Zone - 2  area.

iii) As per our technical specification  Cl.no. 5.5.5, we accept horizontal split casing pump only. Deviation is not accepted.

iv) Kindly confirm submission Quality Plan  for Lalitpur Customer Approval covering Inspection and Testing requirement as per technical specification. You can also include their standard  painting and packing spec in the Quality plan.  

v) Spares qty indicated is per project.
