## 400kV ETC
BOQ for Erection Testing & Commissioning (ETC) Works for 400 kV Switchyard at 400/132 kV s/s for Nabinagar STPP & Extn at 400 kV Nabinagar TPP (BRBCL) Rev 01
Project : 400/132 kV s/s for Nabinagar STPP & Extn at 400 kV Nabinagar TPP (BRBCL)
Customer : NPGC (Nabinagar Power Generating Company Pvt. Ltd.)
This BOQ only covers ETC work for 400 kV Switchyard at 400/132 kV s/s for Nabinagar STPP & Extn at 400 kV Nabinagar TPP (BRBCL) , unloading and storage of all the material required for above Switchyard is covered under separate contract. ETC contractor of 400 kV Switchyard at 400/132 kV s/s for Nabinagar STPP & Extn at 400 kV Nabinagar TPP (BRBCL) package shall ask in writing to unloading and storage contractor for issuance of items/material required for 400 kV Switchyard at 400/132 kV s/s for Nabinagar STPP & Extn at 400 kV Nabinagar TPP (BRBCL). All arrangement for Lifting and shifting of material for ETC for 400 kV Switchyard at 400/132 kV s/s for Nabinagar STPP & Extn at 400 kV Nabinagar TPP (BRBCL) from the storage area shall be in the scope of of the ETC contractor of 400kV Switchyard. Bidder should quote only for ETC work in this BOQ.
S.No. | Voltage Class (kV) | Type | Description | Unit | 400 kV Nabinagar STPP | 400 kV Nabinagar TPP | Total | Unit Price | Total Price
MAIN EQUIPMENTS
1 | 400 kV | Without PIR | SF6, 3 Phase Circuit Breaker alongwith lattice type GS supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling. (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit and Gas leak detector only. Necessary manpower support, tools, tackles and testing kit to be in scope of ETC contractor). | Nos. | 18 | 3 | 21 |  | 0
2 | 400 kV | Without PIR, with CSD | SF6, 3 Phase Circuit Breaker with Controlled switching device alongwith lattice type GS supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling. (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit and Gas leak detector only. Necessary manpower support, tools, tackles and testing kit to be in scope of ETC contractor). | Nos. | 2 | 0 | 2 |  | 0
2.1 |  | CSD | Special cabling between CB and Relay Panel in AC Kiosk | m | 100 | 0 | 100 |  | 0
3 | 400 kV | HCB (Mechanically ganged) | 3 Ph, Isolator, motor/ manual operated complete with 6 nos. of support insulators & terminal connectors without support structure | [5 empty] | 0
3.1 |  |  | - without earth switch | Nos. |  | 0 | 0 |  | 0
3.2 |  |  | - with one earth switch (motor/ manual operated) | Nos. | 54 | 8 | 62 |  | 0
3.3 |  |  | - with two earth switch (motor/ manual operated) | Nos. | 2 | 0 | 2 |  | 0
4 | 400 kV | Upto 2000 A | 1 Ph, Current Transformer (2000 A), dead tank complete with terminal connectors without support structure. | Nos. | 63 | 18 | 81 |  | 0
5 | 400 kV | Above 2000 A | 1 Ph, Current Transformer (3000 A), dead tank complete with terminal connectors without support structure. | Nos. | 42 | 0 | 42 |  | 0
6 | 400 kV |  | 1 Ph, CVT complete with terminal connector without support structure. | Nos. | 33 | 6 | 39 |  | 0
7 | 390/ 360 kV |  | 1 Phase, Gapless type Metal Oxide Surge Arrester complete with surge counter, leakage current meter, insulating base, connecting cable and terminal connectors. | [5 empty] | 0
7.1 |  |  | Low level (upto 8 m height from plinth) | Nos. | 27 | 6 | 33 |  | 0
7.2 |  |  | High level (above 8 m to 10.5 m height from plinth) | Nos. | 18 | 0 | 18 |  | 0
8 | 400 kV | Pedestal type | 1 phase, Wave Trap complete with 3 nos. post insulators per WT with terminal connectors without support structure. | Nos. | 8 | 0 | 8 |  | 0
9 | 400 kV | Solidcore wirh corona ring | Post Insulators complete with corona ring & terminal connectors without support structure | [5 empty] | 0
9.1 |  |  | low level (upto 8 m height from plinth) | Nos. | 266 | 12 | 278 |  | 0
9.2 |  |  | High level (above 8 m to 10.5 m height from plinth) | Nos. | 9 | 0 | 9 |  | 0
10 | 400 kV |  | Dismantling of existing jumpers including TEE connectors, spacers etc. on 400kV HCB Isolators | Lot |  | 2 | 2 |  | 0
11 | 400 kV |  | Dismantling of existing Terminal connectors on 400kV HCB Isolators | nos. |  | 6 | 6 |  | 0
12 | 400 kV |  | Dismantling of existing 4" Al. tube (approx. 10.5 Mtr) to accommodate CTs for Tie section | Lot |  | 6 | 6 |  | 0
13 | BUS BAR MATERIALS | [7 empty] | 0
13.1 | Stringing hardware | [7 empty] | 0
13.1.1 | 400 kV | Double Tension | Tension insulator string with double/single anchoring point , string comprising 2X25 nos. disc with hardware set with all accessories including tension clamp with/ without Turn Buckle set suitable for twin/quad conductor. | Set | 240 | 6 | 246 |  | 0
13.1.2 | 400 kV | Single Suspension | Suspension insulator string comprising 1X25 nos. disc with hardware set with all accessories including drop/through type suspension clamp suitable for single/twin/quad conductor. | Set | 75 | 6 | 81 |  | 0
14 | - | 7/9 SWG | GI Stranded Shield wire including tension clamp, PG clamp and clamping on structure for down conductor, fixing/bolting with earth strip etc to complete. | Km | 4.1 | 0.125 | 4.225 |  | 0
15 | - | ACSR Moose | Conductor complete with Tee connectors for droppers to equipment connections, PG clamps for busbar jumpering, Twin/Quad bundle spacers etc to complete. | Km | 33.6 | 1.65 | 35.25 |  | 0
16 |  | 4.0" | Al Tube (ETC of Al.Tube includes Aluminium welding and bending to be included. Welding sleeve tube will be supplied by BHEL.) | m | 3818 | 261.5 | 4079.5 |  | 0
| ENGINEERED ITEMS | [7 empty] | 0
17 |  |  | A. Cabling including laying, tagging , dressing, ferruling, Glanding, lugging, ,soldering, tapping, jointing, crimping, termination, and drilling/ cutting holes in cable gland plates- laying can be either on trays, supports, underground, buried in ground or through GI pipe over ground, through wall etc. All erection materials viz. ferrules, copper lugs, cable ties / straps, Al. tags, markers, GI / PVC wall sleeves with rubber / nylon bushes and flexible steel conduits shall be supplied by bidder. Cable glands shall be supplied by BHEL. | [5 empty] | 0
17.1 |  |  | Control cables | [5 empty] | 0
17.1.1 |  | PVC | 5Cx2.5 sqmm Cu | km | 38 | 6 | 44 |  | 0
17.1.2 |  | PVC | 4Cx10 sqmm Cu | km | 7 | 1.5 | 8.5 |  | 0
17.1.3 |  | PVC | 10Cx2.5 sqmm Cu | km | 54 | 9.5 | 63.5 |  | 0
17.1.4 |  | PVC | 14Cx2.5 sqmm Cu | km | 6 | 2.5 | 8.5 |  | 0
17.1.5 |  | PVC | 19Cx2.5 sqmm Cu | km | 23 | 1.5 | 24.5 |  | 0
|  | PVC | 4Px0.5 sqmm Cu screened | km | 2 | 0 | 2 |  | 0
17.2 |  |  | Auxiliary Power cables | [5 empty] | 0
17.2.1 |  | PVC | 2Cx2.5 sqmm Cu | km | 13 | 0.5 | 13.5 |  | 0
17.2.2 |  | PVC | 2Cx6 sqmm Al | m | 5 | 1 | 6 |  | 0
17.2.3 |  | PVC | 4Cx6 sqmm Al | m | 7 | 1.5 | 8.5 |  | 0
17.2.4 |  | PVC | 4Cx16 sqmm Al | m | 19 | 1.5 | 20.5 |  | 0
17.2.5 |  | PVC | 3.5Cx70 sqmm Al | m | 20 | 2 | 22 |  | 0
17.2.6 |  | XLPE | 3.5Cx150 sqmm Al | m | 0.5 | 0 | 0.5 |  | 0
17.2.7 |  | XLPE | 3.5Cx300 sqmm Al | m | 1 | 0 | 1 |  | 0
17.2.8 |  | XLPE | 2Cx150 sqmm Al | m | 0.5 | 0 | 0.5 |  | 0
17.2.9 |  | XLPE | 1Cx630 sqmm Al | m | 1.5 | 0 | 1.5 |  | 0
18 |  |  | Marshalling Kiosks & CT / CVT Junction Boxes | [5 empty] | 0
18.1 |  |  | Bay Marshalling Kiosks ( Outdoor, Floor mounted on cable trench) | Nos. | 18 | 2 | 20 |  | 0
18.2 |  |  | CT Junction Box (on foundation/structure) | Nos. | 35 | 6 | 41 |  | 0
18.3 |  |  | VT Junction Box (on foundation/structure) | Nos. | 11 | 2 | 13 |  | 0
14 |  |  | Laying of Cable trays: including bends, tees, elbow, reducers, stiffeners coupler plates, bolting to racks, structure etc. to complete. | [5 empty] | 0
14.1 |  |  | 150 to 750 mm wide, 2.5 M long Ladder type | Nos. | 180 | 24 | 204 |  | 0
14.2 |  |  | 100 to 750 mm wide, 2.5 M long Perforated type | Nos. | 140 | 24 | 164 |  | 0
15 |  |  | Cable Rack work includes welding of galvanised steel racks on inserts of trench walls in trenches in switchyard and control room. Cable rack assembly will be of 2/3/4 tier. | MT | 77 | 6 | 83 |  | 0
16 |  |  | Laying of GI conduits at a depth of 300mm including excavation, backfilling, making and repairing of walls in trenches, cutting, threading, fixing of sockets/ bends where required etc. complete. Both ends of GI conduits shall be closed by plastering. (Payment will be made for the as erected pipe length) | [5 empty] | 0
16.1 |  |  | GI pipe, 50 NB | m | 1280 | 190 | 1470 |  | 0
16.2 |  |  | GI Pipe, 100 NB | m | 4590 | 750 | 5340 |  | 0
17 |  |  | Fixing of GI Pipes on Lattice/ Pipe Stucture including clamping, fixing of sockets/ bends as required etc. complete. Both ends of GI Pipes shall be closed by plastering. (Payment will be made for the as erected pipe length) | [5 empty] | 0
17.1 |  |  | 50 mm dia | m | 50 | 25 | 75 |  | 0
17.2 |  |  | 100 mm dia | m | 50 | 100 | 150 |  | 0
18 |  |  | Earthing material- The earthing includes earthing of all switchyard equipment, towers, pipe structure, cable trenches, fence, pipe electrode for LA, CVT, neutral of transformer & at interconnections of other grids, Control room equipments using necessary Connectors for earthing flats. Earthing clamping shall be carried out by ETC contractor. GS strip including cutting, bending, welding with 40 mm dia MS rod riser/earth strip, applying zinc rich paint, clamping to structure/building wall etc. to complete. Hardware required for connecting flat on pads of structure & equipment included in scope. The Earthing of equipments, Auxiliary Earthmats under Iso/ ES/ CB MOM boxes shall be carried out as per 0370-572-PVE-F-442 | [5 empty] | 0
18.1 |  |  | 75 x 12 mm GI Flat | m | 8350 | 1300 | 9650 |  | 0
18.2 |  |  | 50 x 6 mm GI Flat | m | 2200 | 150 | 2350 |  | 0
19 |  |  | 40 mm Dia MS Rod | MT | 0.5 | 0 | 0.5 |  | 0
20 |  |  | Galvanised steel Lattice Structures including hardwares for Towers, beams & equipment support | MT | 956 | 32 | 988 |  | 0
21 |  |  | Galvanised steel Pipe Structures including hardwares for equipment support | MT | 255 | 25 | 280 |  | 0
0
|  |  | CONTROL EQUIPMENT | [5 empty] | 0
22 |  |  | AC kiosk (Air conditioned kiosk) of Approx. dimension upto 6.5(L) x 3.5(W) and made of sandwich insulated panels with Poly Urethane Foam (PUF) as filler material between polyester pre-coated cold rolled steel. [Only unloading, storage and handling between store & erection place at site has to be considered] | Nos. | 9 | 1 | 10 |  | 0
23 |  |  | 61850 Based Sub station Automation system (Testing and commissioning of relays in scope of panel supplier. Necessary manpower support, tools, tackles and testing equipment to be in scope of ETC contractor). | [5 empty] | 0
23.01 |  |  | 400 kV Line Protection panel (Approx. width 1600 MM) (2 cubicle) | Sets | 6 | 2 | 8 |  | 0
23.02 |  |  | 400 kV GT Protection panel (Approx. width 800 MM) (1 cubicle) | Sets | 3 | 0 | 3 |  | 0
23.03 |  |  | 400 kV ICT Protection panel (Approx. width 1600 MM) (2 cubicle) | Sets | 2 | 0 | 2 |  | 0
23.04 |  |  | 400 kV Bus Reactor Protection panel (Approx. width 1600 MM) (2 cubicle) | Sets | 1 | 0 | 1 |  | 0
23.05 |  |  | 400 kV Tie Protection panel (Approx. width 800 MM) (1 cubicle) | Sets | 8 | 1 | 9 |  | 0
23.06 |  |  | 400 kV BCU panel (Approx. width 800 MM) (1 cubicle) | Sets | 13 | 2 | 15 |  | 0
23.07 |  |  | 400kV Bus Bar Protection panel (Approx. width 1600 MM) (2 cubicle) | Sets | 1 | 0 | 1 |  | 0
23.08 |  |  | 400kV Islanding Protection panel (Approx. width 1600 MM) (2 cubicle) | Sets | 1 | 0 | 1 |  | 0
23.08 |  |  | Energy Metering panel (Approx. width 1600 MM) (2 cubicle) | Sets | 1 | 0 | 1 |  | 0
23.09 |  |  | SAS AUXILIARY Panels (Approx. width 800 MM) (1 cubicle) | Sets | 2 | 0 | 2 |  | 0
23.10 |  |  | Generator Protection Panels (Approx. width 1000 MM) (1 cubicle) | Sets | 15 | 0 | 15 |  | 0
23.11 |  |  | Workstations (PC) | Nos. | 8 | 0 | 8 |  | 0
23.12 |  |  | Laying of Optical fibre Cable (In GI Pipes in Trenches) (GI pipe not in scope of supply) | M | 5000 | 1000 | 6000 |  | 0
23.13 |  |  | Large video screen (1 No.) | No. | 1 | 0 | 1 |  | 0
23.14 |  |  | Laser/ Inkjet/ Dot matrix Black & white Printer(A4) | No | 0 | 0 | 0 |  | 0
23.15 |  |  | Laser/ Inkjet/ Dot matrix Color Printer(A4) | No | 5 | 0 | 5 |  | 0
23.16 |  |  | Laser/ Inkjet/ Dot matrix Black & white Printer(A3) | No | 0 | 0 | 0 |  | 0
23.17 |  |  | Laser/ Inkjet/ Dot matrix Color Printer(A3) | No | 1 | 0 | 1 |  | 0
23.18 |  |  | Inverter | Nos. | 5 | 0 | 5 |  | 0
23.19 |  |  | Time Synchronizing equipment (GPS ) – complete in all respects including antenna, all cables, processing equipment etc. | Nos. | 2 | 0 | 2 |  | 0
23.2 |  |  | Handling & installation of furniture required in switchyard control room & Power house control room for OWS, printer, chairs etc. | Lot | 1 | 0 | 1 |  | 0
23 |  |  | Supplying Rubber mats (Class-A suitable for 1.1 kV as per IS: 15652) and laying in front of Panels | SQ. M | 450 | 0 | 450 |  | 0
0
25 |  |  | Panel Supporting Angles / Channel etc on cable trench in Control Room & Bay Control Room (Including Supply). | MT | 5 | 0 | 5 |  | 0
26 |  |  | Structural Steel Work welded in built up sections like angles, channels & framed work etc including providing cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete | MT | 2 | 0 | 2 |  | 0
27 |  |  | Installing terminal connector wherever equipment installation is not in scope of contractor. Connectors shall be provided by BHEL. Any other ETC work related to items below is not in the scope of this BOQ. | Nos. of Connectors |  |  |  |  | 0
27.1 |  |  | 400/132 kV ICT | Nos. | 12 | 0 | 12 |  | 0
27.2 |  |  | 400 kV Reactor | Nos. | 3 | 0 | 3 |  | 0
27.3 |  |  | 400 KV GT | Nos. | 9 | 0 | 9 |  | 0
28 |  |  | Laying of Optical fibre Cable | [5 empty] | 0
28.1 |  |  | 25NB GI Pipes in Trenches | m |  | 500 | 500 |  | 0
29 |  |  | Supply & ETC of NTPC approved make 2 HP Automatic Start/ Stop type Centrifugal pump and accessories for sump pit | Lot | 1 | 0 | 1 |  | 0
30 |  |  | Supply & ETC of NTPC approved make 0.5 HP Automatic Start/ Stop type Centrifugal pump and accessories for sump pit | Lot | 1 | 0 | 1 |  | 0
31 |  |  | Supply & Mounting of Phase Color Discs, Danger Plate and Identification Plates for bays & Equipments as per IS:2551; 1982 & IS:5; 1978. | Lot | 1 | 0 | 1 |  | 0
|  |  | Total Price | [5 empty] | 0
Following also forms the scope of ETC work in addition to above, but not limited to this.
1 |  |  | Loading / Unloading, verification, handling, shifting to stores, proper storage is NOT included in the scope. Shifting from stores, proper storage, assembly, installation, pre-commissioning test and commissioning tests (As per BHEL FQP) are included in the scope.
2 |  |  | Annexure- 2 (Switchyard Erection guidelines) shall be followed for ETC work.
3 |  |  | All the drawings and documents as per Annexure-1 shall be followed for ETC work.
4 |  |  | Minor Civil works such as modification of civil foundations, making holes in the trenches/ control room building, grouting, fixing of trench material will be in the scope of ETC contractor.
5 |  |  | Removal of gravel, if gravelling is done, for connection of Equipment earthing strip to the existing mat (wherever earthing mat is already laid), and after completion of earthing , contractor should place the gravel to bring it in original shape.
6 |  |  | The quantities given in items mentioned above may undergo a change to any extent.
7 |  |  | Quoted rates are deemed to be inclusive of miscellaneous works viz erection of clamps and connectors.
8 |  |  | All paint , welding electrodes & other consumable by contract supplies shall be part of ETC works. Paint /welding electrode make etc. is subject to BHEL/CUSTOMER site incharge approval.
9 |  |  | Equipment erection (say Isolator ) means complete erection, metallics, post insulator, connectors (expansion/rigid tubular for Al.Tube / single/double/quadraple conductor), connection to the next in line (if connected to overhead busbar or droppers) including PG clamps/Tee connectors etc. This will be clear from the enclosed electrical layout drawings.
10 |  |  | Equipment and tower erection would include supply and erection of miscellanneous items , viz Phase colour discs , labels painting of equipments , phase colour painting , phase marking , bay identification board , danger plates , rubber mats , device number marking on the equipment, keyboard etc as per site requirements. Supply & Mounting of phase color discs & Danger plates shall be as per IS-2551; 1982 & IS 5; 1978.
11 |  |  | Welding of Aluminium tubes ( supply of welding sleeve excluded) as per Annexure-3 is in ETC contractor's scope and joints shall be tested by radiography. Welding and Bending machines and any other equipment will be in ETC Contractor scope.
12 |  |  | Completete ETC package is under the scope of bidder. All TNP including oil filterating machine, cranes etc. required to complete the job shall be provided by bidder only.
13 |  |  | Supervision of erection, Testing & commissioning of one no. Isolator of each type shall be done by supplier, M/s GR Power. Necessary menpower support, tools, tackles etc shall be in the scope of ETC contractor.
14 |  |  | Testing istruments (dully calibrated) have to be arranged by ETC Contractor at it's own cost ( List is only provided for information , if any other instrument not mentioned below but required for sucessful completion of ETC work shall be in ETC contractor's scope) , (However OMICRON or equivalent kit for Numerical relay testing shall be arranged by BHEL.)
15 |  |  | DCRM (OPERATIONAL ANALYZER )
16 |  |  | Contact Resistance Measurement kit (CRM)
17 |  |  | Capacitance and Tan delta measurement Kit
17.1 |  |  | Dew Point Measurement kit
17.2 |  |  | 5kV/1kV Megger
17.3 |  |  | Primary current Injection Kit
17.4 |  |  | Secondary current/Voltgae Injection kit
17.5 |  |  | 1Ph Variac
17.6 |  |  | Multimeters
17.7 |  |  | Clamp on meter
17.8 |  |  | Relay test kit
ALL EQUIPMENTS / MATERIALS SHALL STORED AT NABINAGAR STPP (3X600 MW). EQUIPMENTS/ MATERIALS REQUIRED AT NABINAGAR TPP REQUIRED TO BE SHIFTED BY ETC CONTRACTOR. DISTANCE BETWEEN NABINAGAR STPP AND NABINAGAR TPP IS APPROX. 10 KM.