## Sheet1
BOQ for Erection Testing & Commissioning (ETC) Works
Project : 400kV Bay Extension at Abhishekpatty Substation
Customer : POWERGRID CORPORATION OF INDIA LIMITED
Rev 01
S.No. | Voltage Class (kV) | Type | Description | Unit | Qty. | Unit Price | Total Price
MAIN EQUIPMENTS
1a | 400 kV | With PIR | SF6, 3 Phase, 3150A Circuit Breaker alongwith lattice type GS supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling. (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit and Gas leak detector only. Necessary manpower support, tools, tackles and testing kit to be in scope of ETC contractor). | Nos. | 1 |  | 0
1b | 400 kV | With/Without PIR | Supply of DCRM Kits on retunable basis for testing purpose | Nos. | 1 |  | 0
1c | 400 kV | Without PIR | SF6, 3 Phase, 3150A Circuit Breaker alongwith lattice type GS supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling. (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit and Gas leak detector only. Necessary manpower support, tools, tackles and testing kit to be in scope of ETC contractor). | Nos. | 1 |  | 0
2 | 400 kV | HDB (Electrically ganged) | 3 Ph, Isolator, motor/ manual operated complete with 9 nos. of support insulators & terminal connectors without support structure |  |  |  | 0
2a |  |  | - with one earth switch (motor/ manual operated) | Nos. | 6 |  | 0
3 | 400 kV | 3000 A | 1 Ph, Current Transformer (3000A) , live/dead tank complete with terminal connectors without support structure. | Nos. | 6 |  | 0
4 | 400 kV | 4400pF | 1 Ph, CVT complete with terminal connector without support structure. | Nos. | 3 |  | 0
5 | 336kV |  | 1 Phase, Gapless type Metal Oxide Surge Arrester complete with surge counter, leakage current meter, insulating base, connecting cable and terminal connectors. | Nos. | 3 |  | 0
6 | 400 kV | Pedestal type | 1 phase, Wave Trap complete with 3 nos. post insulators per WT with terminal connectors without support structure. | Nos. | 2 |  | 0
7 | 400 kV | Solidcore wirh corona ring | Post Insulators 8kN complete with corona ring & terminal connectors without support structure | Nos. | 7 |  | 0
8 | BUS BAR MATERIALS
8.1 | Stringing hardware | [5 empty] | 0
8.1.1 | 400 kV | Double Tension | Tension insulator string with double anchoring point , string comprising 2X25 nos. disc with hardware set with all accessories including tension clamp without Turn Buckle set suitable for quad conductor. | Set | 6 |  | 0
8.1.2 | 400 kV | Double Tension | Tension insulator string with double anchoring point , string comprising 2X25 nos. disc with hardware set with all accessories including tension clamp with Turn Buckle set suitable for quad conductor. | Set | 9 |  | 0
8.1.3 | 400 kV | Single Suspension | Suspension insulator string comprising 1X25 nos. disc with hardware set with all accessories including drop type suspension clamp suitable for quad conductor. | Set | 9 |  | 0
8.2 | - | ACSR Moose | Conductor complete with Tee connectors for droppers to equipment connections, PG clamps for busbar jumpering, Twin/Quad bundle spacers etc to complete. | Km | 2.8 |  | 0
8.3 |  | 4.5" | Al Tube (ETC of Al.Tube includes Aluminium welding and bending to be included. Welding sleeve tube will be supplied by BHEL.) | m | 186 |  | 0
ENGINEERED ITEMS
9 |  |  | A. Cabling including laying, tagging , dressing, ferruling, lugging, ,soldering, tapping, jointing, crimping, termination, and drilling/ cutting holes in cable gland plates- laying can be either on trays, supports, underground, buried in ground or through GI pipe over ground, through wall etc. All erection materials viz. ferrules, copper lugs, cable ties / straps, Al. tags, markers, GI / PVC wall sleeves with rubber / nylon bushes and flexible steel conduits shall be supplied by bidder. Glands shall be quoted seprately. |  |  |  | 0
9.1 |  |  | Control cables |  |  |  | 0
9.1.1 |  | PVC | 2Cx2.5 sqmm Cu | Km | 0.5 |  | 0
9.1.2 |  | PVC | 5Cx2.5 sqmm Cu | Km | 2 |  | 0
9.1.3 |  | PVC | 7Cx2.5 sqmm Cu | Km | 1 |  | 0
9.1.4 |  | PVC | 10Cx2.5 sqmm Cu | Km | 1 |  | 0
9.1.5 |  | PVC | 14Cx2.5 sqmm Cu | Km | 0.5 |  | 0
9.1.6 |  | PVC | 19Cx2.5 sqmm Cu | Km | 1 |  | 0
9.2 |  |  | Auxiliary Power cables |  |  |  | 0
9.2.1 |  | PVC | 3.5Cx70 sqmm Al/Cu | Km | 1.1 |  | 0
9.2.2 |  | PVC | 3.5Cx35 sqmm Al/Cu | Km | 0.5 |  | 0
9.2.3 |  | PVC | 4Cx16 sqmm Al/Cu | Km | 4.3 |  | 0
9.2.4 |  | PVC | 4Cx6 sqmm Al/Cu | Km | 0.5 |  | 0
9.2.5 |  | PVC | 2Cx6 sqmm Al/Cu | Km | 0.5 |  | 0
10 |  | PVC | Tin/ Nickel, Nichel/chromium - Plated (coating thickness not less than 10 microns) brass cable glands, double compression heavy-duty type complete with necessary armour clamp & tapered washer etc for the following cables (Bidder's Scope is to supply and fixing) * refer clause 14.3.9, 10,11 of section SE page 33 of 60 |  |  |  | 0
10.1 |  | PVC/ XLPE | 2Cx2.5 sqmm Cu | Nos. | 20 |  | 0
10.2 |  | PVC/ XLPE | 5Cx2.5 sqmm Cu | Nos. | 40 |  | 0
10.3 |  | PVC/ XLPE | 7Cx2.5 sqmm Cu | Nos. | 20 |  | 0
10.4 |  | PVC/ XLPE | 10Cx2.5 sqmm Cu | Nos. | 30 |  | 0
10.5 |  | PVC/ XLPE | 14Cx2.5 sqmm Cu | Nos. | 20 |  | 0
10.6 |  | PVC/ XLPE | 19Cx2.5 sqmm Cu | Nos. | 20 |  | 0
10.7 |  | PVC/ XLPE | 3.5Cx70 sqmm Al/Cu | Nos. | 20 |  | 0
10.8 |  | PVC/ XLPE | 3.5Cx35 sqmm Al/Cu | Nos. | 20 |  | 0
10.9 |  | PVC/ XLPE | 4Cx16 sqmm Al/Cu | Nos. | 50 |  | 0
10.1 |  | PVC/ XLPE | 4Cx6 sqmm Al/Cu | Nos. | 20 |  | 0
10.11 |  | PVC/ XLPE | 2Cx6 sqmm Al/Cu | Nos. | 20 |  | 0
11 |  |  | Installation of Cable transit system for passage of cables from outdoor (switchyard area) to indoor area (building, rooms etc.) | Nos. of cable entries | 4 |  | 0
12 |  |  | Marshalling Kiosks & CT / CVT Junction Boxes |  |  |  | 0
12.1 |  |  | Bay Marshalling Kiosks ( Outdoor, Floor mounted on cable trench) | Nos. | 2 |  | 0
12.2 |  |  | CT Junction Box (on CT structure) | Nos. | 2 |  | 0
12.3 |  |  | VT Junction Box (on VT structure) | Nos. | 1 |  | 0
|  |  | Perforated cable trays for equipment support structure |  |  |  | 0
13 |  |  | Supply of Perforated GI cable trays with all accessories including bends, tees, elbow, reducers, stiffeners coupler plates, bolts/clamps etc and fixing of same with suitable bolt/clamp on equipment pipe support structure for vertical runs of cables |  |  |  | 0
13.1 |  |  | 150 mm wide | m | 35 |  | 0
13.2 |  |  | 200 mm wide | m | 55 |  | 0
14 |  |  | Cable trench material-fabrication of cable support angles and stopper as per enclosed POWERGRID standard drawing C/ENGG/STD/CT-1, erection and painting( after installation with two coats of metal primer comprising of red oxide and Zinc chromate in a synthetic medium followed by two finishing coats of Aluminium paints) of cable rack assembly.Cable rack assembly shall be provided at every 750 mm interval. | MT | 1.4 |  | 0
15 |  |  | Supply of PVC pipes, sockets & bends of class 4 as per IS 4985 and laying at a depth of 250mm including excavation, backfilling, making and repairing of walls in trenches, cutting, threading, fixing of sockets/ bends where required etc. complete. Both ends of PVC conduits shall be closed by plastering. (Payment will be made for the as erected pipe length) |  |  |  | 0
15.1 |  |  | PVC pipe, 50 NB | m | 200 |  | 0
15.2 |  |  | PVC Pipe, 110NB | m | 410 |  | 0
16 |  |  | GI Pipes -Supply of 25 NB GI pipes, sockets & bends and laying of the same on the tier of cable trench between Switchyard panel rooms, cutting, threading, fixing of sockets/ bends where required etc. complete. Both ends of GI Pipes shall be closed by plastering. (Payment will be made for the as erected pipe length) |  |  |  | 0
16.1 |  |  | 25 mm dia | m | 190 |  | 0
17 |  |  | Earthing material- The earthing includes earthing of all switchyard equipment, towers, pipe structure, cable trenches, rod electrode for LA, CVT, neutral of transformer & at interconnections of other grids, Control room & switchyard panel room equipments using necessary Connectors for earthing flats. Earthing clamping shall be carried out by ETC contractor. GS strip including cutting, bending, welding with 40 mm dia MS rod riser/earth strip, applying zinc rich paint, clamping to structure/building wall etc. to complete. The Earthing of equipments, Auxiliary Earthmats under Iso/ ES MOM boxes shall be carried out as per POWERGRID standard drawings |  |  |  | 0
17.1 |  |  | 75 x 12 mm GS Flat | MT | 4 |  | 0
17.2 |  |  | 50 x 6 mm GS Flat | MT | 2 |  | 0
17.3 |  |  | 40 mm Dia MS Rod | m | 500 |  | 0
17.4 |  |  | 40/ 32 mm Dia 3 M MS Rod electrode with test link & earth pit | Nos. | 6 |  | 0
18 |  |  | Galvanised steel Pipe Structures including hardwares for equipment support | MT | 40 |  | 0
19 |  |  | SPR/CONTROL ROOM EQUIPMENT |  |  |  | 0
19.1 |  |  | Control & Relay Panel (Refer note 18) |  |  |  | 0
19.1.1 |  |  | 400kV Circuit Breaker Relay Panel with Auto-Reclose 1 Set = 1 No. Panel | Sets | 2 |  | 0
19.1.2 |  |  | 400kV Line Protection Panel 1 Set = 1 No. Panels | Set | 1 |  | 0
19.2 |  |  | VOID |  |  |  | 0
19.3 |  |  | Communication Equipment (Refer note 18) |  |  |  | 0
19.3.1 |  |  | SDH Equipment Cabinets : 1 No comprising of STM – 4, minimum two MSP protected directions : Base Equipment (Common cards, Cross-connect/control cards, Optical base card, Power supply cards, power cabling, other hardware & accessories including sub-racks, patch cords, DDF etc. fully equipped including interface cards and Tributary cards and equipment Cabinet) Optical Interface card for Optical Line interface card (to support minimum 150 kms) - 2 Nos. Tributary Cards : E1 Interface card (Minimum 16 interfaces per card) - 2 Nos. Tributary Cards : Ethernet interfaces 10/100 Mbps with Layer-2 switching (Minimum 4 interfaces per card.) - 1 No. | No | 1 |  | 0
19.3.2 |  |  | Drop/Insert Multiplexer Equipment Cabinets : 1 No comprising of Base Equipment (Common cards, Power supply cards, power cabling, other hardware & accessories including sub-racks, etc. fully equipped including subscriber line interface cards and equipment cabinet) 2 Nos. = 1 Lot Subscriber Line Interface Cards : 2 wire (sub/sub) voice channel cards (min 8 channels per card) - 2 Nos. Subscriber Line Interface Cards : 4 wire (E&M) voice channel cards (min 8 channels per card) - 2 Nos. Subscriber Line Interface Cards : Asynchronous Sub Channels data cards (minimum 4 channels per card) - 2 Nos. Subscriber Line Interface Cards : Synchronous data card (NX64kbps) - 1 No. | No | 1 |  | 0
19.3.3 |  |  | Main Distribution Frame (100 pairs) | No. | 1 |  | 0
19.4 |  |  | PLCC Equipments (Refer note 18) |  |  |  | 0
19.4.1 |  |  | Coupling device(Phase to Phase) | Nos. | 1 |  | 0
19.4.2 |  |  | HF cable | m | 250 |  | 0
19.4.3 |  |  | Carrier equipment (for speech + protection and speech +data) (Analogue type )--- Single Channel PLC terminal for Speech + Protection (1 set = 1 no. panel) | Set | 1 |  | 0
19.4.4 |  |  | Carrier equipment (for speech + protection and speech +data) (Analogue type )-- Single Channel PLC terminal for Speech + Data | Nos. | 0 |  | 0
19.4.5 |  |  | Protection Coupler (shall be mounted on item at S.No. 15.5.3 above) | Nos. | 1 |  | 0
19.4.6 |  |  | Digital Protection Coupler (shall be mounted on item at S.No. 15.5.3 above) | Nos. | 1 |  | 0
19.4.7 |  |  | 4 wire telephone instrument(along with telephone wiring ) -- 4 wire telephone set with connecting cables | Nos. | 1 |  | 0
19.4.8 |  |  | 4 wire telephone instrument(along with telephone wiring ) --5 Pair Telephone Cables, armoured ,0.5 sq. mm annealed copper conductor and petroleum jelly filled with polyethene outer jackets (refer description at S. No. 9) | m | 500 |  | 0
19.4.9 |  |  | Testing & maintenance equipment(print test kit only) (Unloading, Storage & handing over in ETC contractor scope) | Set | 1 |  | 0
20 |  |  | Illumination System |  |  |  | 0
20.1 |  |  | Lighting panel (outdoor) Type ACP-1 | Nos. | 1 |  | 0
20.2 |  |  | Lighting panel (outdoor) Type ACP-2 | Nos. | 2 |  | 0
20.3 |  |  | Lighting panel (outdoor) Type ACP-3 | Nos. | 1 |  | 0
20.4 |  |  | Sub lighting panel (outdoor) Type SLP | Nos. | 2 |  | 0
20.5 |  |  | AC Power Panel (Indoor) Type ACPP | Nos. | 1 |  | 0
20.6 |  |  | Switchboard with 4 nos. NO switch and 1 no. switch | Nos. | 1 |  | 0
20.7 |  |  | Lighting fixtures and receptacles including junction Box & lighting wires & flexible conduits (if required) from junction box to lighting fixture, mounting arrangement and other accessories / materials as required for complete installation and commissioning of lighting fixture. Lighting fixture type - SF1 | Nos. | 10 |  | 0
20.8 |  |  | Lighting fixtures and receptacles including junction Box & lighting wires & flexible conduits (if required) from junction box to lighting fixture, mounting arrangement and other accessories / materials as required for complete installation and commissioning of lighting fixture. Lighting fixture type - SF2 | Nos. | 20 |  | 0
20.9 |  |  | Illumination system for Switchyard Panel Room (size : 6m x 4m x 3.5m) -Lighting fixtures and receptacles including junction Box & lighting wires & flexible conduits (if required) from junction box to lighting fixture, mounting arrangement and other accessories / materials as required for complete installation and commissioning of indoor lighting fixture | Nos. | 4 |  | 0
21 |  |  | Supplying Insulating mats (Class-A for 1.1kV as per IS: 15652-2006) and laying in front of Panels in switchyard panel room | SQ. M | 18 |  | 0
22 |  |  | Phase marker, Danger Plate and Identification Plates for bays & Equipments | Lot | 1 |  | 0
23 |  |  | Supplying Rubber mats (Class-A suitable for 1.1 kV as per IS: 15652) and laying in front of Panels | SQ. M | 18 |  | 0
24 |  |  | Panel Supporting Angles / Channel etc on cable trench in Control Room & Bay Control Room (Including Supply). | MT | 0.5 |  | 0
25 |  |  | Laying of Optical fibre Cable in 25NB GI Pipes in Trenches | m | 1000 |  | 0
26 |  |  | Unloading, storage & handing over of Essential/ Mandatory spares to Customer as per Annexure-I | Lot | 1 |  | 0
27 |  |  | Unloading, storage and carrying of AC units from storage area to SPR | Nos. | 2 |  | 0
|  |  | Total Amount (Rs.) |  |  |  | 0
Following also forms the scope of ETC work in addition to above, but not limited to this.
1 |  |  | Loading / Unloading, verification, handling, shifting to & from stores, proper storage, assembly, installation, pre-commissioning test and commissioning tests (As per BHEL FQP) are included in the scope.
2 |  |  | POWERGRID Technical specification for switchyard erection, technical specification, section: SE, (C/ENGG/SPEC/SE REV. NO. 08) is enclosed. In case of any conflict, the POWERGRID technical specification shall be followed. The equipment earthing shall be done as per POWERGRID standard drawings (Standard Earthing Details).
3 |  |  | All the drawings and documents as per Annexure-2 shall be followed for ETC work.
4 |  |  | Minor Civil works such as modification of civil foundations, making holes in the trenches/ control room building, grouting, fixing of trench material will be in the scope of ETC contractor.
5 |  |  | Removal of gravel, if gravelling is done, for connection of Equipment earthing strip to the existing mat (wherever earthing mat is already laid), and after completion of earthing , contractor should place the gravel to bring it in original shape.
6 |  |  | The quantities given in items mentioned above may undergo a change to any extent.
7 |  |  | Quoted rates are deemed to be inclusive of miscellaneous works viz erection of clamps and connectors.
8 |  |  | All paint , welding electrodes & other consumable by contract supplies shall be part of ETC works. Paint /welding electrode make etc. is subject to BHEL/CUSTOMER site incharge approval.
9 |  |  | Equipment erection (say Isolator ) means complete erection, metallics, post insulator, connectors (expansion/rigid tubular for Al.Tube / single/double/quadraple conductor), connection to the next in line (if connected to overhead busbar or droppers) including PG clamps/Tee connectors etc. This will be clear from the enclosed electrical layout drawings.
10 |  |  | Equipment and tower erection would include supply and erection of miscellanneous items , viz Phase colour discs , labels painting of equipments , phase colour painting , phase marking , bay identification board , danger plates , rubber mats , device number marking on the equipment, keyboard etc as per site requirements. Supply & Mounting of phase color discs & Danger plates shall be as per IS-2551; 1982 & IS 5; 1978.
11 |  |  | Welding of Aluminium tubes ( supply of welding sleeve excluded) is in ETC contractor's scope and joints shall be tested by radiography. Welding and Bending machines and any other equipment will be in ETC Contractor scope.
12 |  |  | Completete ETC package is under the scope of bidder. All TNP including oil filterating machine, cranes etc. required to complete the job shall be provided by bidder only.
13 |  |  | Supervision of erection, Testing & commissioning of one no. Isolator of each type shall be done by supplier, M/s GR Power. Necessary menpower support, tools, tackles etc shall be in the scope of ETC contractor.
14 |  |  | Testing istruments (dully calibrated) have to be arranged by ETC Contractor at it's own cost ( List is only provided for information , if any other instrument not mentioned below but required for sucessful completion of ETC work shall be in ETC contractor's scope) , (However OMICRON or equivalent kit for Numerical relay testing shall be arranged by BHEL.)
15 |  |  | DCRM (OPERATIONAL ANALYZER )
16 |  |  | Contact Resistance Measurement kit (CRM)
17 |  |  | Capacitance and Tan delta measurement Kit
17.1 |  |  | Dew Point Measurement kit
17.2 |  |  | 5kV/1kV Megger
17.3 |  |  | Primary current Injection Kit
17.4 |  |  | Secondary current/Voltgae Injection kit
17.5 |  |  | 1Ph Variac
17.6 |  |  | Multimeters
17.7 |  |  | Clamp on meter
17.8 |  |  | Relay test kit
18 |  |  | Testing and commissioning is in the scope of OEM