## For Indian bidders
PROJECT: 2X500 MW NEW NEYVELI TPP (SG PACKAGE)
BOQ CUM PRICE SCHEDULE - HT XLPE POWER CABLE
FOR INDIGENOUS BIDDERS
MAIN SUPPLY
11KV/11KV & 3.3KV/3.3KV (non-effectively earthed system) grade 90°C rating heavy duty XLPE power cable single or multicore, stranded compacted circular aluminium conductor H2 grade class 2, conductor screened by triple extruded semi conducting compound, cross linked poly ethylene insulated, insulation screened by triple extruded semi conducting compound (strippable) in combination with copper tape (for multicore cables) laid up FRLSH inner sheath with extruded PVC compound type ST 2 (for multicore cables), armoured (galvanized single core round steel wire armour for multicore cables and Non-magnetic hard drawn aluminium single round wire conforming to H4 grade for single core cables) and overall sheath with extruded FRLS PVC (type ST-2) cable complying with IS 7098 (part-2), IS-8130, IS-5831 & IS-3975.
S. NO. | Cable Sizes | Drum Length | Total Quantity | LOT-1 Quantity | Unit price (Ex-works) Rs. | Total price (Ex-works) Rs. | Excise Duty (Rs.) | CST/VAT@....% (Rs.) | Freight Charges (Including Service Tax, if any) @........% of quoted total Ex-Works Price (Rs.) | Total FOR Site Price (Rs.)
1 | 11 kV armoured cables
1.1 | 3C – 240 Sq. mm | 13 drums of 600 Meters, 10 drums of 500 Meters & 1 drum of 400 Meters | 13200 Meters | 13200 Meters |  |  | NIL AGAINST PAC. Refer SCC Sl. No.18A.
1.2 | 1C – 240 Sq. mm | 3 drums of 600 Meters & 6 drums of 400 Meters | 4200 Meters | 4200 Meters
2 | 3.3 kV armoured cables
2.1 | 1C – 240 Sq. mm | 2 drums of 500 Meters | 1000 Meters | 1000 Meters |  |  | NIL AGAINST PAC. Refer SCC Sl. No.18A.
2.2 | 3C – 240 Sq. mm | 1 drum of 500 Meters | 500 Meters | 500 Meters
TOTAL | [5 empty] | `
Notes :
1. Quantities indicated above shall be known as Order Quantities. The variation in quantities of all sizes put together shall be limited to (+/- )30% of the total contract value till completion of supplies for 2x500 MW NEYVELI NEW THERMAL POWER STATION (NNTPS) Project.
2. The bidder shall indicate the unit price of each type and size of cables listed as per the BOQ in the Price Schedule enclosed with this specification. The unit prices shall apply for adjustment of variation in quantity as stipulated above.
3. Lot-I quantities indicated above (in case the cable quantities are to be released for manufacture in more than one lot), or Order Quantity (in case the quantities are cleared for manufacture in one lot only) shall be cleared for manufacturing along with LOI. However, manufacturing of the cables shall be taken up by the successful bidder only after approval of technical and quality documentation and shall be completed within four months from the date of approval of documentation. Subsequent lots shall be cleared for manufacture based on progress of engineering and site requirements. A lead-time of three months shall be given for completion of supply for each subsequent lot from the date of clearance of the quantities.
4. Overall tolerance on total dispatched quantity of each size shall be (-) 2% and (+) 0% Cables consumed for testing and inspection shall be to bidder’s account.
5. Bidder shall indicate unit price of cables inclusive of type test charges. No separate charges shall be payable for type tests.
6. Standard drum length shall be 400m, 500m & 600m. Tolerance on individual drum length shall be (±) 5%

## For Foreign bidders
PROJECT: 2X500 MW NEW NEYVELI TPP (SG PACKAGE)
BOQ CUM PRICE SCHEDULE - HT XLPE POWER CABLE
FOR FOREIGN BIDDERS (Bidder to indicate currency …….)
MAIN SUPPLY
11KV/11KV & 3.3KV/3.3KV (non-effectively earthed system) grade 90°C rating heavy duty XLPE power cable single or multicore, stranded compacted circular aluminium conductor H2 grade class 2, conductor screened by triple extruded semi conducting compound, cross linked poly ethylene insulated, insulation screened by triple extruded semi conducting compound (strippable) in combination with copper tape (for multicore cables) laid up FRLSH inner sheath with extruded PVC compound type ST 2 (for multicore cables), armoured (galvanized single core round steel wire armour for multicore cables and Non-magnetic hard drawn aluminium single round wire conforming to H4 grade for single core cables) and overall sheath with extruded FRLS PVC (type ST-2) cable complying with IS 7098 (part-2), IS-8130, IS-5831 & IS-3975.
S. NO. | Cable Sizes | Drum Length | Total Quantity | LOT-1 Quantity | UNIT FOB PRICE | TOTAL FOB PRICE
1 | 11 kV armoured cables
1.1 | 3C – 240 Sq. mm | 13 drums of 600 Meters, 10 drums of 500 Meters & 1 drum of 400 Meters | 13200 Meters | 13200 Meters
1.2 | 1C – 240 Sq. mm | 3 drums of 600 Meters & 6 drums of 400 Meters | 4200 Meters | 4200 Meters
2 | 3.3 kV armoured cables
2.1 | 1C – 240 Sq. mm | 2 drums of 500 Meters | 1000 Meters | 1000 Meters
2.2 | 3C – 240 Sq. mm | 1 drum of 500 Meters | 500 Meters | 500 Meters
TOTAL | [5 empty] | `
Notes :
1. Quantities indicated above shall be known as Order Quantities. The variation in quantities of all sizes put together shall be limited to (+/- )30% of the total contract value till completion of supplies for 2x500 MW NEYVELI NEW THERMAL POWER STATION (NNTPS) Project.
2. The bidder shall indicate the unit price of each type and size of cables listed as per the BOQ in the Price Schedule enclosed with this specification. The unit prices shall apply for adjustment of variation in quantity as stipulated above.
3. Lot-I quantities indicated above (in case the cable quantities are to be released for manufacture in more than one lot), or Order Quantity (in case the quantities are cleared for manufacture in one lot only) shall be cleared for manufacturing along with LOI. However, manufacturing of the cables shall be taken up by the successful bidder only after approval of technical and quality documentation and shall be completed within four months from the date of approval of documentation. Subsequent lots shall be cleared for manufacture based on progress of engineering and site requirements. A lead-time of three months shall be given for completion of supply for each subsequent lot from the date of clearance of the quantities.
4. Overall tolerance on total dispatched quantity of each size shall be (-) 2% and (+) 0% Cables consumed for testing and inspection shall be to bidder’s account.
5. Bidder shall indicate unit price of cables inclusive of type test charges. No separate charges shall be payable for type tests.
6. Standard drum length shall be 400m, 500m & 600m. Tolerance on individual drum length shall be (±) 5%