	PSGSG109
	SPECIFICATIONS FOR

Pull Rod Assy.
	Drg.No.
	RD DG 4 35 1351 1300

	
	
	Date 
	20.06.14

	
	
	
	

	
	
	Product
	CGSM-145

	1.0


	APPLICATION:

Tubular insulator with metal flanges is a part of a high voltage, heavy duty switchgear. The component is intended for a 145 kV AC, 50 Hz System.


	2.0


	2.1

2.1.1
2.1.2
	SPECIFICATION:

TUBE MATERIAL

The POLYESTER lining used for tube shall have following properties:

#

Property

Unit

Value

1

Density
g/ccm                        
~1.3
2

Tensile strength       
MPa                 
~1000           
3
Impulse dielectric Strength
kV/mm               
≥ 16
4
Relative permittivity                      
-
~3.4

5
Dielectric loss factor   
%
~0.4  
6
SHRINKAGE15 HR160 oC
%  
( 2
7
SHRINKAGE
%
< 0.5  
8
Water Absorption    
%
< 0.5  

9
Water Absorption @ 1000C                    

%

< 0.5  

Type of Fiber: Aramid / Kevlar shall be used as fiber. The material shall be resistant against arced SF6 gas.

	Page

1/3

	PSGSG109.doc 
	
	     Signature









           Contd..

	PSGSG109
	SPECIFICATIONS FOR

Pull Rod Assy.
	Drg.No.
	RD DG 4 35 1351 1300

	
	
	Date 
	20.06.14

	
	
	
	

	
	
	Product
	CGSM-145

	2.2
3.0


	2.1.3

2.1.4

2.1.5

2.2.1

2.2.2

2.2.3

3.1

3.2 


	Manufacturing process: The fibers shall be wound and impregnated with hot curing epoxy resin in vacuum/ pressure. The casting shall be void free and shall achieve required electrical and mechanical properties. The epoxy used shall be compatible to arced SF6 gas.

The processed material shall have good Chemical resistance against organic and inorganic acids. 

The shape of the tube shall be in accordance to the approved drawing.

METAL INSERTS 

Profiled metal inserts as per approved drawing shall be machined using NC machining from mechanical grade aluminum alloy as per (DIN/BIS/IS standards).  

The aluminum flanges shall be glued to the epoxy tube using a hot curing adhesive (compatible to arced SF6 gas) and joined as per the practices of the supplier.

The bonding between insulator and metal flanges shall be done without roll pins /threaded bolts/ cross bolts. The bonding shall not only withstand specified mechanical forces but also offer leak tightness for use in differential pressure application.

FACTORY TEST

Dimensional report.
Mechanical load bearing capability (Tensile, ~30 kN+ 10%) for the glued joints. The joint shall have an ultimate strength of  ~50 kN .


	 Page

 2/3
	PSGSG109.doc 
	       Signature

           

	PSGSG109
	SPECIFICATIONS FOR

Pull Rod Assy.
	Drg.No.
	RD DG 4 35 1351 1300

	
	
	Date 
	20.06.14

	
	
	
	

	
	
	Product
	CGSM-145

	4.0 

5.0


	5.1

5.2

5.3

5.4


	QUALIFYING REQUIREMENTS:

The supplier shall be of national / International repute with proven record and should have supplied similar material for gas insulated system applications at least for last three years. 

GENERAL

Metal Flanges shall be free from sharp corners. Wherever not specified in the drawing, a radius of R 0.5mm shall be provided at unspecified corner/Edge.

The components shall be packed individually in appropriate packing with moisture absorbents so as to prevent transit damages. 
The components shall be guaranteed against all manufacturing defects.

In case of doubts in specifications, the supplier shall contact BHEL for clarifications.



	Page

3/3

	PSGSG109.doc 
	
	  Signature




1
1

