	PSGSG105
	SPECIFICATIONS FOR

INSULATING TUBE ASSY.
	Drg.No.
	RD DG 4 35 0520 6110

	
	
	Date 
	23.09.14

	
	
	
	

	
	
	Product
	GSM-245

	1.0


	APPLICATION:

Tubular insulator with metal flanges is a part of a high voltage, heavy duty switchgear. The component is intended for a 245 kV AC, 50 Hz System.

	2.0


	2.1

2.1.1
2.1.2
2.1.3

2.1.4

2.1.5
	SPECIFICATION:

TUBE MATERIAL
The POLYESTER lining used for tube shall have following properties:

#

Property

Unit

Value

1

Density
g/ccm                        
~1.3
2

Tensile strength       
MPa                 
>100       
3
Impulse dielectric Strength
kV/mm               
≥ 16
4
Relative permittivity                      
-
~3.4

5
Dielectric loss factor   
%
~0.4  
6
SHRINKAGE
%
< 0.5  
7
Water Absorption    
%
< 0.5  

8
Water Absorption @ 1000C                    

%

< 0.5  

Type of Fiber: Aramid / Kevlar or a combination of these fibers. The material shall be resistant against arced SF6.
Manufacturing process: The fibers shall be wound and impregnated with hot curing epoxy resin in vacuum/ pressure. The casting shall be void free and shall achieve required electrical and mechanical properties. The epoxy used shall be compatible to arced SF6 gas.

The processed material shall have good Chemical resistance against organic and inorganic acids. 

The shape of the tube shall be in accordance to the approved drawing.



	Page

1/2

	PSGSG105.doc 
	
	     Signature









           Contd..

	PSGSG105
	SPECIFICATIONS FOR

INSULATING TUBE ASSY.
	Drg.No.
	RD DG 4 35 0520 6110

	
	
	Date 
	23.09.14

	
	
	
	

	
	
	Product
	GSM-245

	2.2
3.0
4.0

5.0


	2.2.1

2.2.2

2.2.3

2.2.4
3.1

3.2 
5.1

5.2

5.3
	METAL INSERTS 

Profiled metal inserts as per approved drawing shall be machined using NC machining from aluminium alloy with good electrical conductivity and mechanical properties as per (DIN/BIS/IS standards).  

The aluminium flanges shall be glued to the epoxy tube using a hot curing adhesive (compatible to arced SF6 gas) and joined as per the practices of the supplier.

The bonding between insulator and metal flanges shall be done without roll pins /threaded bolts/ cross bolts. The bonding shall withstand specified mechanical forces. 

Helical grooves are only optional, made on the flanges for better bonding between aluminium flanges and insulating tube. 

FACTORY TEST
Dimensional report.
Mechanical load bearing capability (Tensile, 30 kN+ 10%).

QUALIFYING REQUIREMENTS

The supplier shall be of national / International repute with proven record and should have supplied insulating tubes for high voltage gas insulation applications in past years. The supplier must submit along with the quotation a few references to whom the supplier has supplied a similar material. 

GENERAL

Metal Flanges shall be free from sharp corners. Wherever not specified in the drawing, a radius of R 0.5mmo shall be provided at unspecified corner/Edge.

The components shall be packed individually in appropriate packing so as to prevent transit damages.

The components shall be guaranteed against all manufacturing defects.

	 Page

 2/2
	PSGSG105.doc 
	       Signature

           


1
1

