                                                                             Encl to  Indent No 83212   26-7-08
 Specification No.- PDB1A-S-00              
The scope of supply includes design ,  manufacturing , supply and supervision of  installation/commissioning at our works  of the power distribution boards as per following specs :

1. The Power distribution board shall be comprising of one incomer panel and the outgoing module feeder panels 11 nos  with hinged type doors at front  for each feeder module. The incomer panel approx.  dimension shall be W X H X D = 800 X2390X1300 mm and each  outgoings panel approx. dims shall be W X H X D = 800 X2390X560 mm .

2. The incomer ACB shall be draw-out type and outgoings shall be fixed type.
3. The details of various feeders rating with their components are as per  annexure  : 1A-F.

4. The details /specifications of equipments/components for various feeders are as per annexure  : 1A-C.

5. The material for all the bus-bars and cable conductors shall be copper and shall be provided with PVC heat shrinkable tube insulation .

6. The incomer ACB panel for PDB1A shall be on right end . 

7. All the switchgears ,indicating lamps , selector switches  SFUs shall be of Siemens or L & T make only . The make of ACB shall be L & T , Siemens  or G.E. Power only. The makes of all the voltmeters and ammeters shall be A.E. only.

8. The indicating lamps , voltmeters , ammeters, selector switches, control knobs/operating handles of SFUs , pushbuttons , front of ACB etc shall be on the front door of the respective feeder modules.

9. The panels shall be conforming to IP-43 protection  IS 13947 part 1 1993.

10. The input supply system available is 3 phase 3 wire 415 V +/-10%, 50 Hz A.C.

11. The Power distribution board  assly. shall be conforming to  IS   8623 part-1 and part -2 (1993). The testing of the panel shall be as per the I.S.  practice .

12. The thickness of the M.S sheet  C/R  for the doors shall be at least 3.15 mm and for the remaining sides shall be at least 2.50 mm as per IS 1730 -1989. The structure of the panels should be rigid enough to bear the vibrations and environmental conditions .

13. The hinged doors of the panels shall be properly earthed using flexible wires .

14. The panels shall be painted internally by paint shade white  and externally by paint shade grey ( RAL 7032) .

15. The structure of the panels shall be chemically pretreated before painting.

16. The earthing-busbar of suitable sizes shall be provided throughout the length of the panels.

17. The min/max amb. Temp. is 2 deg C/46 deg C. The Min/Max relative humidity is 9/94 %.

18. The vendor shall get approved the mechanical drgs. , electrical drg., component details  of the panels before mfg. the same within one month of placement of the P.O. .

19. Three sets of drgs elect schematics and panel layouts, panel wiring diagrams and catalogs / operation / maint manuals of the various equipments/ components used shall be required with delivery.

20. The T.C. and G.C. for one year after installation /commissioning shall be required.

.                                                                Encl to Indent No 83212 26-7-08

Specification No.- PDB2A-S-00              
The scope of supply includes design ,  manufacturing , supply and supervision of  installation/commissioning at our works  of the power distribution boards as per following specs :

1. The Power distribution board shall be comprising of incomer panel one no. and the outgoing module feeder panels 11 nos  with hinged type doors at front  for each feeder module. The incomer panel approx. dimension shall be W X H X D = 800 X2390X1300 mm and each  outgoings panel approx. dims shall be W X H X D = 800 X2390X560 mm .

2. The incomer ACB shall be draw-out type and outgoings shall be fixed type. 

3. The details of various feeders rating with their components are as per annexure  : 2A-F.

4. The details /specifications of equipments/components for various feeders are as per annexure  : 2A-C.

5. The material for all the bus-bars and cable conductors shall be copper and shall be provided with PVC heat shrinkable tube insulation .

6. The incomer ACB panel for PDB1A shall be on left  end . 

7. All the switchgears ,indicating lamps , selector switches  SFUs shall be of Siemens or L & T make only . The make of ACB shall be L & T , Siemens  or G.E. Power only. The makes of all the voltmeters and ammeters shall be A.E. only.

8. The indicating lamps , voltmeters , ammeters, selector switches, control knobs/operating handles of SFUs , pushbuttons , front of ACB etc shall be on the front door of the respective feeder modules.

9. The panels shall be conforming to IP-43 protection  IS 13947 part 1 1993.

10. The input supply system available is 3 phase 3 wire 415 V +/-10%, 50 Hz A.C.

11. The Power distribution board  assly. shall be conforming to  IS   8623 part-1 and part -2 (1993). The testing of the panel shall be as per the I.S.  practice .

12. The thickness of the M.S sheet  C/R  for the doors shall be at least 3.15 mm and for the remaining sides shall be at least 2.50 mm as per IS 1730 -1989. The structure of the panels should be rigid enough to bear the vibrations and environmental conditions .

13. The hinged doors of the panels shall be properly earthed using flexible wires .

14. The panels shall be painted internally by paint shade white  and externally by paint shade grey ( RAL 7032) .

15. The structure of the panels shall be chemically pretreated before painting.

16. The earthing-busbar of suitable sizes shall be provided throughout the length of the panels.

17. The min/max amb. Temp. is 2 deg C/46 deg C. The Min/Max relative humidity is 9/94 %.

18. The vendor shall get approved the mechanical drgs. , electrical drg., components details  of the panels before mfg. the same within one month of placement of the P.O. .

19. Three sets of drgs elect schematics and panel layouts, panel wiring diagrams and catalogs / operation / maint.  manuals of the various equipments/ components used shall be required with delivery.

20. The T.C. and G.C. for one year after installation /commissioning shall be required.

                                                                   Encl to  Indent No 83212 26-7-08
 Specification No.- PDB3A-S-00              
The scope of supply includes design ,  manufacturing , supply and supervision of  installation/commissioning at our works  of the power distribution boards as per following specs :

1. The Power distribution board shall be comprising of total 5 nos  panels with  incomer feeder module  and the outgoing feeder module panels with hinged type of doors at front for each feeder module. The approx. dims for each panel  shall be    W X H X D = 800 X2390X560 mm .

2. The details of various feeders rating with their components are as per annexure  : 3A-F.

3. The details /specifications of equipments/components for various feeders are as per annexure  : 3A-C.

4. The material for all the bus-bars and cable conductors shall be copper and shall be provided with PVC heat shrinkable tube insulation .

5. The incomer SFU  panel for PDB3A shall be on right end . 

6. All the switchgears ,indicating lamps , selector switches  SFUs shall be of Siemens or L & T make only .  The makes of all the voltmeters and ammeters shall be A.E. only.

7. The indicating lamps , voltmeters , ammeters, selector switches, control knobs/operating handles of SFUs , pushbuttons etc shall be on the front door of the respective feeder modules.

8. The panels shall be conforming to IP-43 protection  IS 13947 part 1 1993.

9. The input supply system available is 3 phase 3 wire 415 V +/-10%, 50 Hz A.C.

10. The Power distribution board  assly. shall be conforming to  IS   8623 part-1 and part -2 (1993). The testing of the panel shall be as per the I.S.  practice .

11. The thickness of the M.S sheet  C/R  for the doors shall be at least 3.15 mm and for the remaining sides shall be at least 2.50 mm as per IS 1730 -1989. The structure of the panels should be rigid enough to bear the vibrations and environmental conditions .

12. The hinged doors of the panels shall be properly earthed using flexible wires .

13. The panels shall be painted internally by paint shade white  and externally by paint shade grey ( RAL 7032) .

14. The structure of the panels shall be chemically pretreated before painting.

15. The earthing-busbar of suitable sizes shall be provided throughout the length of the panels.

16. The min/max amb. Temp. is 2 deg C/46 deg C. The Min/Max relative humidity is 9/94 %.

17. The vendor shall get approved the mechanical drgs. , electrical drg.,component details  of the panels before mfg. the same within one month of placement of the P.O. .

18. Three sets of drgs elect schematics and panel layouts, panel wiring diagrams and catalogs / operation / maint manuals of the various equipments/ components used shall be required with delivery.

19. The T.C. and G.C. for one year after installation /commissioning shall be required.


- 3 -


