## Chhegaon
BOQ for Erection Testing & Commissioning (ETC) Works Rev 00
Project :CHHEGAON
Customer : MPPTCL
S.No. | Voltage Class (kV) | Type | Description | Unit | Qty | Rate (Rs) | Amount (Rs)
MAIN EQUIPMENTS
1 | 400 kV | Without PIR | SF6, 3 Phase Circuit Breaker alongwith lattice type GS supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling. (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit only. Necessary manpower support, tools, tackles as per notes to be in scope of ETC contractor). | Nos. | 1 |  | 0
2 | 220 kV | Without PIR | SF6, 3 Phase Circuit Breaker alongwith lattice type GS supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling. (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit only. Necessary manpower support, tools, tackles as per notes to be in scope of ETC contractor). | Nos. | 1 |  | 0
3 | 33 kV | Without PIR | vacuum, 3 Phase Circuit Breaker alongwith lattice type GS supporting structure, terminal connectors, Breaker Control Cabinets, ladder and interpole cabling. (Supervision of Erection, Testing and commissioning will be done by supplier. Supplier will bring Timing kit only. Necessary manpower support, tools, tackles as per notes to be in scope of ETC contractor). | Nos. | 1 |  | 0
4 | 400 kV | HCB (Electrically ganged) | 3 Ph, Isolator, motor/ manual operated complete with 6 nos. of support insulators & terminal connectors and interpole cabling without support structure |  |  |  | 0
4.1 |  |  | - without earth switch | Nos. | 1 |  | 0
5 | 400 kV | Pantograph (Electrically ganged) | 3 Ph, Isolator, motor/ manual operated complete with 3 nos. of support insulators and 3 nos. of rotating insulators , terminal connectors and interpole cabling without support structure. |  |  |  | 0
5.1 |  |  | - with one earth switch (manual operated) | Nos. | 3 |  | 0
6 | 220 kV | HDB ( Mechanicaly ganged) | 3 Ph, Isolator, manual operated complete with 9 nos. of support insulators & terminal connectors and interpole cabling without support structure |  |  |  | 0
6.1 |  |  | - without earth switch | Nos. | 4 |  | 0
7 | 33 kV | HDB ( Mechanicaly ganged) | 3 Ph, Isolator, manual operated complete with 9 nos. of support insulators & terminal connectors and interpole cabling without support structure |  |  |  | 0
7.1 |  |  | - without earth switch | Nos. | 2 |  | 0
8 | 400 kV | Upto 2000 A | 1 Ph, Current Transformer , live/dead tank complete with terminal connectors without support structure. | Nos. | 3 |  | 0
9 | 220 kV | Upto 1600 A | 1 Ph, Current Transformer , live/dead tank complete with terminal connectors without support structure. | Nos. | 3 |  | 0
10 | 33 kV | Upto 1200 A | 1 Ph, Current Transformer , live/dead tank complete with terminal connectors without support structure. | Nos. | 6 |  | 0
11 | 33 kV | PT | 1 Ph, PT complete with terminal connector without support structure. | Nos. | 3 |  | 0
12 | 390 kV |  | 1 Phase, Gapless type Metal Oxide Surge Arrester complete with surge counter, leakage current meter, insulating base, connecting cable and terminal connectors without structure | Nos. | 3 |  | 0
13 | 198 kV |  | 1 Phase, Gapless type Metal Oxide Surge Arrester complete with surge counter, leakage current meter, insulating base, connecting cable and terminal connectors without structure | Nos. | 3 |  | 0
14 | 36/33/30kV |  | 1 Phase, Gapless type Metal Oxide Surge Arrester complete with surge counter, leakage current meter, insulating base, connecting cable and terminal connectors. without structure | Nos. | 6 |  | 0
15 | 400 kV | Solidcore wirh corona ring | Post Insulators complete with corona ring & terminal connectors without support structure | Nos. | 13 |  | 0
16 | 220 kV | Solidcore wirtout corona ring | Post Insulators complete with terminal connectors without support structure | Nos. | 36 |  | 0
17 | 33 kV | Solidcore | Post Insulators complete with terminal connectors without support structure | Nos. | 7 |  | 0
18 | BUS BAR MATERIALS | [5 empty] | 0
18.1 | Stringing hardware | [5 empty] | 0
18.1.1 | 220 kV | SingleTension | Tension insulator string with double/single anchoring point , string comprising 1X14 nos. Disc with hardware set with all accessories including tension clamp with/ without Turn Buckle set suitable for single/twin conductor. | Set | 75 |  | 0
18.1.2 | 400 kV | Double Tension | Tension insulator string with double/single anchoring point , string comprising 2X24 nos. disc with hardware set with all accessories including tension clamp with/ without Turn Buckle set suitable for twin/quad conductor. | Set | 30 |  | 0
18.1.3 | 400 kV | Single Suspension | Suspension insulator string comprising 1X23 nos. disc with hardware set with all accessories including drop/through type suspension clamp suitable for twin/quad conductor. | Set | 9 |  | 0
18.1.4 | 220 kV | Single Suspension | Suspension insulator string comprising 1X13 nos. disc with hardware set with all accessories including drop/through type suspension clamp suitable for single/twin conductor. | Set | 6 |  | 0
18.1.5 | - | - | Sag compensating spring | Nos. | 9 |  | 0
18.2 | - | 7/9 SWG | GI Stranded Shield wire including tension clamp, PG clamp and clamping on structure for down conductor, fixing/bolting with earth strip etc to complete. | Km | 0.7 |  | 0
18.3 | - | ACSR Moose | Conductor complete with Tee connectors for droppers to equipment connections, PG clamps for busbar jumpering, Twin/Quad bundle spacers etc to complete. | Km | 4 |  | 0
18.4 |  | 4.0" | Al Tube (ETC of Al.Tube includes Aluminium welding and bending to be included. Welding sleeve will be supplied by BHEL.) | m | 350 |  | 0
| ENGINEERED ITEMS | [5 empty] | 0
19 |  |  | A. Cabling including laying, tagging , dressing, ferruling, lugging, ,soldering, tapping, jointing, crimping, termination, and drilling/ cutting holes in cable gland plates- laying can be either on trays, supports, underground, buried in ground or through GI pipe over ground, through wall etc. All erection materials viz. ferrules, copper lugs, cable ties / straps, Al. tags, markers, GI / PVC wall sleeves with rubber / nylon bushes and flexible steel conduits shall be supplied by bidder. Glands shall be quoted seprately. |  |  |  | 0
19.1 |  |  | Control cables |  |  |  | 0
19.1.1 |  | PVC, ARMOURED | 4Cx4 sqmm Cu | Km | 3 |  | 0
19.1.2 |  | PVC, ARMOURED | 4Cx10 sqmm Cu | Km | 3 |  | 0
19.1.3 |  | PVC, ARMOURED | 4Cx2.5 sqmm Cu | Km | 3 |  | 0
19.1.4 |  | PVC, ARMOURED | 12Cx2.5 sqmm Cu | Km | 3 |  | 0
19.1.5 |  | PVC, ARMOURED | 19Cx2.5 sqmm Cu | Km | 3 |  | 0
19.1.6 |  | PVC, ARMOURED | 2Cx2.5 sqmm Cu | Km | 3 |  | 0
19.2 |  |  | Auxiliary Power cables |  |  |  | 0
19.2.1 |  | PVC, ARMOURED | 3.5Cx300 sqmm Al | Km | 1 |  | 0
20 |  |  | Tin/ Nickel / Nichel/chromium - Plated (coating thickness not less than 10 microns) brass cable glands, double compression heavy-duty type complete with necessary armour clamp & tapered washer etc for the following cables (Bidder's Scope is to supply and fixing) |  |  |  | 0
20.1 |  | PVC, ARMOURED | 4Cx4 sqmm Cu | Nos. | 30 |  | 0
20.2 |  | PVC, ARMOURED | 4Cx10 sqmm Cu | Nos. | 30 |  | 0
20.3 |  | PVC, ARMOURED | 4Cx2.5 sqmm Cu | Nos. | 30 |  | 0
20.4 |  | PVC, ARMOURED | 12Cx2.5 sqmm Cu | Nos. | 30 |  | 0
20.5 |  | PVC, ARMOURED | 19Cx2.5 sqmm Cu | Nos. | 30 |  | 0
20.6 |  | PVC, ARMOURED | 2Cx2.5 sqmm Cu | Nos. | 30 |  | 0
20.7 |  | PVC, ARMOURED | 3.5Cx300 sqmm Al | Nos. | 4 |  | 0
21 |  |  | Marshalling Kiosks & CT / CVT Junction Boxes |  |  |  | 0
21.1 |  |  | MK(Outdoor, Floor mounted on cable trench) | Nos. | 1 |  | 0
21.2 |  |  | Junction Box 36 Ways (on foundation) | Nos. | 1 |  | 0
21.3 |  |  | Junction Box 64 Ways (on foundation) | Nos. | 1 |  | 0
21.4 |  |  | Junction Box 128 Ways (on foundation) | Nos. | 6 |  | 0
22 |  |  | Supply & Laying of PVC conduits at a depth of 300mm including excavation, backfilling, cutting, threading, fixing of sockets/ bends where required etc. complete. Both ends of PVC conduits shall be closed by plastering. (Payment will be made for the as erected pipe length) |  |  |  | 0
22.1 |  |  | PVC pipe, 50 mm Dia Class-4 | m | 300 |  | 0
22.2 |  |  | Socket Bend for 50 mm dia PVC pipe class-4 | Nos. | 35 |  | 0
22.3 |  |  | 60 degree bend for 50 mm dia PVC pipe class-4 | Nos. | 10 |  | 0
24 |  |  | Earthing material- The earthing includes earthing of all switchyard equipment, towers, pipe/lattice structure, cable trenches, fence, pipe electrode for LA, CVT, neutral of transformer & at interconnections of other grids, Control room equipments using necessary Connectors for earthing flats. Earthing clamping shall be carried out by ETC contractor. GS strip including cutting, bending, welding with 75X8 riser/earth strip, applying zinc rich paint, clamping to structure/building wall etc. to complete. Hardware required for connecting flat on pads of structure & equipment included in scope. The Earthing of equipments, Auxiliary Earthmats under Iso/ ES/ CB MOM boxes shall be carried out as per details provided later. |  |  |  | 0
23.1 |  |  | 50 x 6 mm GI Flat | m | 4160 |  | 0
23.2 |  |  | 75 x 8 mm GI Flat (Riser) | m | 250 |  | 0
24 |  |  | Galvanised steel Lattice Structures including hardwares for Towers, beams & equipment support | MT | 150 |  | 0
25 |  |  | Galvanised steel Pipe Structures including hardwares for equipment support | MT | 4 |  | 0
26 |  |  | CONTROL ROOM EQUIPMENT |  |  |  | 0
26.1 |  |  | 415V, Sub-ACDB with 1 incomers | Set | 1 |  | 0
27 |  |  | Conventional Hardwired Panels ( Non-61850 Based system) (Testing and commissioning of relays in scope of panel supplier. Necessary manpower support, tools, tackles and testing equipment to be in scope of ETC contractor). |  |  |  | 0
27.1 |  |  | 400KV side of 400/220/33kV ICT Bay Control Panel (Approx Width 1000 MM) (1 Set consists of 1 Nos. Panels) | Set | 1 |  | 0
27.2 |  |  | 220KV side of 400/220/33kV ICT Bay Control Panel (Approx Width 1000 MM) (1 Set consists of 1 Nos. Panels) | Set | 1 |  | 0
28 |  |  | Conventional Hardwired Panels (Non-61850 Based system) (Testing and commissioning of relays in scope of panel supplier. Necessary manpower support, tools, tackles and testing kit to be in scope of ETC contractor). All the other works are in ETC contractor's scope. |  |  |  | 0
28.1 |  |  | 400KV side of 400/220/33kV ICT Bay Protection Panel (Approx Width 800 MM) (1 Set consists of 2 Nos. Panels) | Set | 1 |  | 0
28.2 |  |  | 220KV side of 400/220/33kV ICT Bay Protection Panel (Approx Width 800 MM) (1 Set consists of 1 Nos. Panels) | Set | 1 |  | 0
28.3 |  |  | 33KV side of 400/220/33kV ICT Bay Control and Protection Panel (Approx Width 800 MM) (1 Set consists of 1 Nos. Panels) | Set | 1 |  | 0
29 |  |  | Supplying Rubber mats (Class-A suitable for 1.1 kV as per IS: 15652) and laying in front of Panels | SQ. M | 4 |  | 0
30 |  |  | Panel Supporting Angles / Channel etc on cable trench in Control Room & Bay Control Room (Including Supply). | MT | 0.25 |  | 0
31 |  |  | Structural Steel Work welded in built up sections like angles, channels & framed work etc including providing cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete | MT | 0.5 |  | 0
32 |  |  | Dismantling of chain link fence around the 400/ 220/ 33 kV switchyard and handing over the material to Customer/BHEL store. | m | 50 |  | 0
33 | 400/220/33 kV | Outdoor | 315 MVA, 3-Ph, Auto Transformer complete in all respects alongwith OLTC, Marshalling Kiosk, terminal connectors, accessories, with oil. Work includes unloading, erection of all auxiliaries, viz turrets, bushings, terminal connectors, filling of oil, oil filteration, Oil testing, laying of cable from Transformer auxiliaries to MK & OLTC etc as required to complete the installation of transformer. | Nos. | 1 |  | 0
33.1 | 33kV |  | 1 Ph, surge capacitor complete with terminal connector without support structure. | Nos. | 3 |  | 0
34 |  |  | Dragging charges of above mentioned ICT (1 No.) upto plinth | m | 35 |  | 0
35 | 33kV/ 415V | Outdoor | LT Auxilairy Oil filled Transformers. Work includes unloading, dragging upto plinth, erection of all auxiliaries, viz bushings, terminal connectors, filling of oil, oil filtration, oil testing, testing & Commissioning etc. |  |  |  | 0
|  |  | upto 630kVA but more than 200kVA rating | Nos. | 1 |  | 0
MECHANICAL ITEMS | [6 empty] | 0
36 |  |  | Unloading, Storage and handling at Site of Nitrogen Injection Fire Protection System as per following Details of Site. Tentative Bill of Material for Nitrogen Injection Fire Protection System is as per Annexure-3. |  |  |  | 0
|  |  | 315 MVA 400/220/33 kV Transformer | Nos. | 1 |  | 0
Lighting System | [6 empty] | 0
37 |  |  | ETC of following Illumination items |  |  |  | 0
37.1 |  |  | Lighting Fixture with HPSV/HPMH (1X250/2X250 watt) | Nos. | 10 |  | 0
37.2 |  |  | Lighting Fixture complete with fitting arrangement (CFL 36 Watt) | Nos. | 3 |  | 0
37.3 |  |  | 1 Phase Main switch with fuse link and 4 connectors | Nos. | 3 |  | 0
37.4 |  |  | Tubular Pole For Lighting Fixtures | Nos. | 3 |  | 0
Total Amount | [5 empty] | 0
Following also forms the scope of ETC work in addition to above, but not limited to this.
1 | Loading / Unloading, verification, handling, shifting to & from stores, proper storage, assembly, installation, pre-commissioning test and commissioning tests (As per BHEL FQP) are included in the scope.
2 | Annexure- 2 (Switchyard Erection guidelines) shall be followed for ETC work.
3 | All the drawings and documents as per Annexure-1 shall be followed for ETC work.
4 | Minor Civil works such as modification of civil foundations, making holes in the trenches/ control room building, grouting, fixing of trench material will be in the scope of ETC contractor.
5 | Removal of gravel, if gravelling is done, for connection of Equipment earthing strip to the existing mat (wherever earthing mat is already laid), and after completion of earthing , contractor should place the gravel to bring it in original shape.
6 | The quantities given in items mentioned above may undergo a change to any extent.
7 | Quoted rates are deemed to be inclusive of miscellaneous works viz erection of clamps and connectors.
8 | All paint , welding electrodes & other consumable by contract supplies shall be part of ETC works. Paint /welding electrode make etc. is subject to BHEL/CUSTOMER site incharge approval.
9 | Equipment erection (say Isolator ) means complete erection, metallics, post insulator, connectors (expansion/rigid tubular for Al.Tube / single/double/quadraple conductor), connection to the next in line (if connected to overhead busbar or droppers) including PG clamps/Tee connectors etc. This will be clear from the enclosed electrical layout drawings.
10 | Equipment and tower erection would include supply and erection of miscellanneous items , viz Phase colour discs , labels painting of equipments , phase colour painting , phase marking , bay identification board , danger plates , rubber mats , device number marking on the equipment, keyboard etc as per site requirements. Supply & Mounting of phase color discs & Danger plates shall be as per IS-2551; 1982 & IS 5; 1978.
11 | Welding of Aluminium tubes ( supply of welding sleeve excluded) is in ETC contractor's scope and joints shall be tested by radiography. Welding and Bending machines and any other equipment will be in ETC Contractor scope.
12 | Completete ETC package is under the scope of bidder. All TNP including oil filterating machine, cranes etc. required to complete the job shall be provided by bidder only.
13 | Supervision of erection, Testing & commissioning of one no. Isolator of each type shall be done by equipment supplier. Necessary manpower support, tools, tackles etc shall be in the scope of ETC contractor.
14 | Testing istruments (dully calibrated) have to be arranged by ETC Contractor at it's own cost ( List is only provided for information , if any other instrument not mentioned below but required for sucessful completion of ETC work shall be in ETC contractor's scope) , (However OMICRON or equivalent kit for Numerical relay testing shall be arranged by BHEL.)
14.1 | DCRM (OPERATIONAL ANALYZER )
14.2 | Contact Resistance Measurement kit (CRM)
14.3 | Capacitance and Tan delta measurement Kit
14.4 | Dew Point Measurement kit
14.5 | 5kV/1kV Megger
14.6 | Primary current Injection Kit
14.7 | Secondary current/Voltgae Injection kit
14.8 | 1Ph Variac
14.9 | Multimeters
14.10 | Clamp on meter
14.11 | Relay test kit
14.12 | SF6 Filling & Evacuating trolley